SECTION 13850 (28 31 00)

FIRE & GAS DETECTION AND ALARM SYSTEM

ENGINEERING SPECIFICATION

INTELLIGENT REPORTING FIRE & GAS DETECTION SYSTEM

PART 1	GENERAL

1.1	RELATED SECTIONS

A.	Section 13800 - Building Automation and Control.

B.	Section 13900 (21 00 00) - Fire Suppression.

C.	Section (27 15 00) - (Fire Alarm Communications Horizontal Cabling).

1.2	DESCRIPTION

A.	The fire alarm system shall comply with requirements of NFPA Standard 72 for Protected   Premises Signaling Systems except as modified and supplemented by this specification.  The system shall be electrically supervised and monitor the integrity of all conductors.

B.	The fire alarm system shall be manufactured by an ISO 9001:2008 certified company and meet the requirements of BS EN9001: ANSI/ASQC Q9001-1994

C.	The FACP and peripheral devices shall be manufactured 100% by a single U.S. manufacturer (or division thereof).   It’s acceptable for peripheral devices to be manufactured outside of the U.S. by a division of the U.S. based parent company.

D.	The system and its components shall be Underwriters Laboratories, Inc. listed under the appropriate UL testing standard as listed herein for fire alarm applications and the installation shall be in compliance with the UL listing.

E.	The installing company shall employ NICET (minimum Level II Fire Alarm Technology) technicians on site to guide the final checkout and to ensure the systems integrity.

1.3	GUARANTY:

A.	The fire alarm control panel, voice panels and any head-end equipment shall have a manufacturer’s warranty of a minimum of 3 years.

1.4	POST CONTRACT MAINTENANCE:

A.	Complete maintenance and repair service for the fire and gas detection system shall be available from a factory trained authorized representative of the manufacturer of the major equipment for a period of five (5) years after expiration of the guaranty.

B.	As part of the bid/proposal, include a quote for a maintenance contract to provide all maintenance, required tests, and list pricing for any replacement products included on the bill of materials, along with the list pricing for products not on the bill of materials; if test and inspection rates are different than full service rates the bid/proposal shall include pricing for all levels for a minimum period of five (5) years  Rates and costs shall be valid for the period of five (5) years after expiration of the guaranty.

C.	Include also a quote for unscheduled maintenance/repairs, including hourly rates for technicians trained on this equipment, and response travel costs for each year of the maintenance period. Submittals that do not identify all post contract maintenance costs will not be accepted. Rates and costs shall be valid for the period of five (5) years after expiration of the guaranty.

1.5	APPLICABLE STANDARDS AND SPECIFICATIONS:

A.	The specifications and standards listed below form a part of this specification. The system shall fully comply with the latest issue of these standards, if applicable.

B.	National Fire Protection Association (NFPA) - USA:

| No. 12 | Extinguishing Systems (low and high) |
| --- | --- |
| No. 12A | Halon 1301 Extinguishing Systems |
| No. 13 | Sprinkler Systems |
| No. 15 | Water Spray Systems |
| No. 16 | Foam / Water Deluge and Spray Systems |
| No. 17 | Dry Chemical Extinguishing Systems |
| No. 17A | Wet Chemical Extinguishing Systems |
| No. 2001 | Clean Agent Extinguishing Systems |
| No. 70 | National Electric Code |
| No. 72 | National Fire Alarm Code |
| No. 90A | Air Conditioning Systems |
| No. 92A | Smoke Control Systems |
| No. 92B | Smoke Management Systems in Malls, Atria, Large Areas |
| No. 101 | Life Safety Code |

C.	Underwriters Laboratories Inc. (UL) - USA:

| No. 268 | Smoke Detectors for Fire Protective Signaling Systems |
| --- | --- |
| No. 864 | Control Units for Fire Protective Signaling Systems |
| No. 2572 | Mass Notification Systems |
| No. 217 | Smoke Detectors, Single and Multiple Station |
| No. 228 | Door Closers - Holders for Fire Protective Signaling Systems |
| No. 268A | Smoke Detectors for Duct Applications |
| No. 521 | Heat Detectors for Fire Protective Signaling Systems |
| No. 464 | Audible Signaling Appliances |
| No. 38 | Manually Actuated Signaling Boxes |
| No. 1481 | Power Supplies for Fire Protective Signaling Systems |
| No. 346 | Waterflow Indicators for Fire Protective Signaling Systems |
| No. 1076 | Control Units for Burglar Alarm Proprietary Protective Signaling Systems |
| No. 1971 | Visual Notification Appliances |
| No. 2017 | Standard for General-Purpose Signaling Devices and Systems |
| No.60950 | Safety of Information Technology Equipment |

D.	Local and State Building Codes.

E.	All requirements of the Authority Having Jurisdiction (AHJ).

1.6	APPROVALS:

A.	The system shall have proper listing and/or approval from the following nationally recognized agencies:

| UL | Underwriters Laboratories, Inc |
| --- | --- |
| ULC | Underwriters Laboratories Canada |
| FM | Factory Mutual |
| FM 6320 | Factory Mutual Gas Detection System |
| NYFD | New York Fire Department |
| CSFM | California State Fire Marshal |

B.	The system shall be listed by the national agencies as suitable for extinguishing release applications. The system shall support release of low pressure CO2.

C.	The system shall be certified for seismic applications in accordance with the International Building Code (IBC).  For OSHPD applications in California the system shall be Pre-Approved for seismic applications.  The basis for qualification of seismic approval shall be via shake table testing.

D.	The system shall be approved for Marine Applications and carry the following certifications:

1.	USCG United States Coast Guard

2.	Lloyd’s Register

3.	ABS American Bureau of Shipping

E.	The System shall be FM 6320 (Factory Mutual) approved as a Gas Detection system when employed with the FMM-4-20 monitor module and industry standard 4-20 mA gas detectors.

PART 2.0	PRODUCTS

2.1	Main Fire Alarm Control Panel or Network Node:

A.	Main FACP or network node shall be a NOTIFIERJohnson ControlsHoneywell Model NFS2-3030IFC2-3030XLS3000 and shall contain a microprocessor based Central Processing Unit (CPU) and power supply. The CPU shall communicate with and control the following types of equipment used to make up the system: intelligent addressable smoke and thermal (heat) detectors, addressable modules, printer, annunciators, and other system controlled devices.

B.	In conjunction with intelligent Loop Control Modules and Loop Expander Modules, the main FACP shall perform the following functions:

1.	Supervise and monitor all intelligent addressable detectors and monitor modules connected to the system for normal, trouble and alarm conditions.

2.	Supervise all initiating signaling and notification circuits throughout the facility by way of connection to addressable monitor and control modules.

3.	Detect the activation of any initiating device and the location of the alarm condition.  Operate all notification appliances and auxiliary devices as programmed.  In the event of CPU failure, all SLC loop modules shall fallback to degrade mode.  Such degrade mode shall treat the corresponding SLC loop control modules and associated detection devices as conventional two-wire operation.  Any activation of a detector in this mode shall automatically activate associated Notification Appliance Circuits.

.

2.2	System Capacity and General Operation

A.	The FACP shall be capable of communicating on Noti-Fire-Net over a Local Area Network (LAN) or Wide Area Network (WAN) utilizing a peer-to-peer, inherently regenerative communication format and protocol.  The network shall support communication speed up to 100 Mb and support up to 200 panels / nodes per network.

B.	The control panel shall be capable of expansion of up to 10 SLC loops.  Each module shall support up to  318 analog/addressable devices for a maximum system capacity of 3180 points.

C.	The Fire Alarm Control Panel shall include a full featured operator interface control and annunciation panel that shall include a backlit 640-character liquid crystal display, individual, color coded system status LEDs, and a QWERTY style alphanumeric keypad for the field programming and control of the fire alarm system.  Said LCD shall also support graphic bit maps capable of displaying the company name and logo of either the owner or installing company.

D.	All programming or editing of the existing program in the system shall be achieved without special equipment and without interrupting the alarm monitoring functions of the fire alarm control panel.

E.	The FACP shall be able to provide the following software and hardware features:

1.	Pre-signal and Positive Alarm Sequence:  The system shall provide means to cause alarm signals to only sound in specific areas with a delay of the alarm from 60 to up to 180 seconds after start of alarm processing.  In addition, a Positive Alarm Sequence selection shall be available that allows a 15-second time period for acknowledging an alarm signal from a fire detection/initiating device.  If the alarm is not acknowledged within 15 seconds, all local and remote outputs shall automatically activate immediately.

2.	Smoke Detector Pre-alarm Indication at Control Panel: To obtain early warning of incipient or potential fire conditions, the system shall support a programmable option to determine system response to real-time detector sensing values above the programmed setting. Two levels of Pre-alarm indication shall be available at the control panel: alert and action.

3.	Alert: It shall be possible to set individual smoke detectors for pre-programmed pre-alarm thresholds.  If the individual threshold is reached, the pre-alarm condition shall be activated.

4.	Action: If programmed for Action and the detector reaches a level exceeding the pre-programmed level, the control panel shall indicate an action condition. Sounder bases installed with either heat or smoke detectors shall automatically activate on action Pre-Alarm level, with general evacuation on Alarm level.

5.	The system shall support a detector response time to meet world annunciation requirements of less than 3 seconds.

6.	Device Blink Control:  Means shall be provided to turn off detector/module LED strobes for special areas.

7.	NFPA 72 Smoke Detector Sensitivity Test: The system shall provide an automatic smoke detector test function that meets the sensitivity testing requirements of NFPA 72.

8.	Programmable Trouble Reminder: The system shall provide means to automatically initiate a reminder that troubles exist in the system. The reminder will appear on the system display and (if enabled) will sound a piezo alarm.

9.	On-line or Off-line programming: The system shall provide means to allow panel programming either through an off-line software utility program away from the panel or while connected and on-line. The system shall also support upload and download of programmed database and panel executive system program to a Personal Computer/laptop. A single change to one CPU database shall not require a database download to other CPUs.

10.	History Events:  The panel shall maintain a history file of the last 4000 events, each with a time and date stamp.  History events shall include all alarms, troubles, operator actions, and programming entries.  The control panels shall also maintain a 1000 event Alarm History buffer, which consists of the 1000 most recent alarm events from the 4000 event history file.

11.	Smoke Control Modes: The system shall provide means to perform FSCS mode Smoke Control to meet NFPA-92A and 90B and HVAC mode to meet NFPA 90A.

12.	The system shall provide means for all SLC devices on any SLC loop to be auto programmed into the system by specific address. The system shall recognize specific device type ID's and associate that ID with the corresponding address of the device.

13.	Passwords and Users: The system shall support two password levels, master and user.  Up to 9 user passwords shall be available, each of which may be assigned access to the programming change menus, the alter status menus, or both.  Only the master password shall allow access to password change screens.

14.	Block Acknowledge: The system shall support a block Acknowledge for Trouble Conditions

15.	Sensitivity Adjust: The system shall provide Automatic Detector Sensitivity Adjust based on Occupancy schedules including a Holiday list of up to 15 days.

16.	Environmental Drift Control: The system shall provide means for setting Environmental Drift Compensation by device.  When a detector accumulates dust in the chamber and reaches an unacceptable level but yet still below the allowed limit, the control panel shall indicate a maintenance alert warning.  When the detector accumulates dust in the chamber above the allowed limit, the control panel shall indicate a maintenance urgent warning.

17.	Custom Action Messages:  The system shall provide means to enter up to 100 custom action messages of up to 160 characters each.  It shall be possible to assign any of the 100 messages to any point.

18.	Local Mode: If communication is lost to the central processor the system shall provide added survivability through the intelligent loop control modules.  Inputs from devices connected to the SLC and loop control modules shall activate outputs on the same loop when the inputs and outputs have been set with point programming to participate in local mode or when the type codes are of the same type: that is, an input with a fire alarm type code shall activate an output with a fire alarm type code.

19.	Read status preview - enabled and disabled points: Prior to re-enabling points, the system shall inform the user that a disabled device is in the alarm state.  This shall provide notice that the device must be reset before the device is enabled thereby avoiding activation of the notification circuits.

20.	Custom Graphics: When fitted with an LCD display, the panel shall permit uploading of a custom bit-mapped graphic to the display screen.

21.	Multi-Detector and Cooperating Detectors: The system shall provide means to link one detector with up to two detectors at other addresses on the same loop in cooperative multi-detector sensing.  There shall be no requirement for sequential addresses on the detectors and the alarm event shall be a result of all cooperating detectors chamber readings.

22.	ACTIVE EVENT:  The system shall provide a Type ID called FIRE CONTROL for purposes of air-handling shutdown, which shall be intended to override normal operating automatic functions.  Activation of a FIRE CONTROL point shall cause the control panel to (1) initiate the monitor module Control-by-Event, (2) send a message to the panel display, history buffer, installed printer and annunciators, (3) shall not light an indicator at the control panel, (4) Shall display ACTIVE on the LCD as well a display a FIRE CONTROL Type Code and other information specific to the device.

23.	NON-FIRE Alarm Module Reporting: A point with a type ID of NON-FIRE shall be available for use for energy management or other non-fire situations.  NON-FIRE point operation shall not affect control panel operation nor shall it display a message at the panel LDC.  Activation of a NON-FIRE point shall activate control by event logic but shall not cause any indication on the control panel.

24.	Mass Notification Override:The system shall be UL 2572 listed for Mass Notification and shall be capable, based on the Risk Analysis, of being programmed so that Mass Notification/Emergency Communications events take precedence over fire alarm events.

25.	Security Monitor Points:  The system shall provide means to monitor any point as a type security.

26.	One-Man Walk Test: The system shall provide both a basic and advanced walk test for testing the entire fire alarm system.  The basic walk test shall allow a single operator to run audible tests on the panel.  All logic equation automation shall be suspended during the test and while annunciators can be enabled for the test, all shall default to the disabled state. During an advanced walk test, field-supplied output point programming will react to input stimuli such as CBE and logic equations.  When points are activated in advanced test mode, each initiating event shall latch the input.  The advanced test shall be audible and shall be used for pull station verification, magnet activated tests on input devices, input and output device and wiring operation/verification.

27.	Control By Event Functions: CBE software functions shall provide means to program a variety of output responses based on various initiating events.  The control panel shall operate CBE through lists of zones.  A zone shall become listed when it is added to a point's zone map through point programming. Each input point such as detector, monitor module or panel circuit module shall support listing of up to 10 zones into its programmed zone map.

28.	Permitted zone types shall be general zone, releasing zone and special zone.  Each output point (control module, panel circuit module) can support a list of up to 10 zones including general zone, logic zone, releasing zone and trouble zone.  It shall be possible for output points to be assigned to list general alarm.  Non-Alarm or Supervisory points shall not activate the general alarm zone.

29.	1000 General Zones: The system shall support up to 1000 general purpose software zones for linking inputs to outputs.  When an input device activates, any general zone programmed into that device's zone map will be active and any output device that has an active general zone in its map will be active.  It shall also be possible to use general zone as arguments in logic equations.

30.	1000 Logic Equations: The system shall support up to 1000 logic equations for AND, OR, NOT, ONLY1, ANYX, XZONE or RANGE operators that allow conditional I/O linking.  When any logic equation becomes true, all output points mapped to the logic zone shall activate.

31.	100 trouble equations per device:  The system shall provide support for up to 100 trouble equations for each device, which shall permit programming parameters to be altered, based on specific fault conditions.  If the trouble equation becomes true, all output points mapped to the trouble zone shall activate.

32.	Control-By-Time: A time based logic function shall be available to delay an action for a specific period of time based upon a logic input with tracking feature.  A latched version shall also be available.  Another version of this shall permit activation on specific days of the week or year with ability to set and restore based on a 24 hour time schedule on any day of the week or year.

33. 	Multiple agent releasing zones: The system shall support up to 10 releasing zones to protect against 10 independent hazards. Releasing zones shall provide up to three cross-zone and four abort options to satisfy any local jurisdiction requirements.

34.	Alarm Verification, by device, with timer and tally:  The system shall provide a user-defined global software timer function that can be set for a specific detector.  The timer function shall delay an alarm signal for a user-specified time period and the control panel shall ignore the alarm verification timer if another alarm is detected during the verification period.  It shall also be possible to set a maximum verification count between 0 and 20 with the "0" setting producing no alarm verification.  When the counter exceeds the threshold value entered, a trouble shall be generated to the panel.

- Secure/Access Operation: The system shall have the capability of configuring input modules to monitor status of door contact or other security type sensors. These input modules shall be able to be commanded from the normally ‘Secure’ state to an ‘Access’ state. While in the secure state, the module will transmit alarm conditions to the controller, which shall be annunciated on the LCD and LED displays. The modules shall be placed into the Access state either through the LCD display or through predefined operator keys. While in the Access state, all alarms from the module will be shunted. Placing the module into the access state shall cause a discrete LED associated with input point to flash, but no other trouble or disable condition will be annunciated. Change from Secure to Access and reverse shall be transmitted to the central monitoring station on a per zone basis. Systems that cause or indicate a trouble or disable condition are unacceptable.

F.	Network Communication

1.	The FACP shall be capable of communicating on Noti-Fire-Net over a Local Area Network (LAN) or Wide Area Network (WAN) utilizing a peer-to-peer, inherently regenerative communication format and protocol.  The network shall support communication speed up to 100 Mb and support up to 200 panels/nodes per network.

- The FACP shall be capable of communicating with a Distributed Control System

G.	Central Processing Unit

1.	The Central Processing Unit shall contain and execute all control-by-event (including Boolean functions including but not limited to AND, OR, NOT, ANYx, and CROSSZONE) programs for specific action to be taken if an alarm condition is detected by the system. Such control-by-event programs shall be held in non-volatile programmable memory, and shall not be lost with system primary and secondary power failure.

2.	The Central Processing Unit shall also provide a real-time clock for time annotation, to the second, of all system events. The time-of-day and date shall not be lost if system primary and secondary power supplies fail.

3.	The CPU shall be capable of being programmed on site without requiring the use of any external programming equipment. Systems that require the use of external programmers or change of EPROMs are not acceptable.

4.	The CPU shall provide an EIA-232 interface between the fire alarm control panel and the UL Listed Electronic Data Processing (EDP) peripherals.

5.	The CPU shall provide two EIA-485 ports for the serial connection to annunciation and control subsystem components.

6.	The EIA-232 serial output circuit shall be optically isolated to assure protection from earth ground.

H.	Display

1.	The system display shall provide a 640-character backlit alphanumeric Liquid Crystal Display (LCD). It shall also provide eleven Light-Emitting-Diodes (LEDs) that indicate the status of the following system parameters: AC POWER, FIRE ALARM, PREALARM, SECURITY, SUPERVISORY, SYSTEM TROUBLE, OTHER EVENT, SIGNALS SILENCED, POINT DISABLED, CONTROLS ACTIVE, and CPU FAILURE.

2.	The system display shall provide a QWERTY style keypad with control capability to command all system functions, entry of any alphabetic or numeric information, and field programming. Two different password levels with up to ten (one Master and nine User) passwords shall be accessible through the display interface assembly to prevent unauthorized system control or programming.

I.	Loop (Signaling Line Circuit) Control Module:

1.	The Loop Control Module shall monitor and control a minimum of 318254 intelligent addressable devices. This includes 159127 intelligent detectors (Ionization, Photoelectric, or Thermal) and 159127 monitor or control modules.

2.	The Loop Control Module shall contain its own microprocessor and shall be capable of operating in a local/degrade mode (any addressable device input shall be capable of activating any or all addressable device outputs) in the unlikely event of a failure in the main CPU.

3.	Each SLC shall be capable of NFPA 72 Style 4, Style 6, or Style 7 (Class A or B) wiring. Fault isolation modules shall be installed between each addressable SLC device per the manufacturers installation instructions. Systems which cannot provide full loop loading in Style 7 configurations are not acceptable.

4.	The SLC interface board shall receive analog or digital information from all intelligent detectors and shall process this information to determine whether normal, alarm, or trouble conditions exist for that particular device. Each SLC Loop shall be isolated and equipped to annunciate an Earth Fault condition.  The SLC interface board software shall include software to automatically maintain the detector's desired sensitivity level by adjusting for the effects of environmental factors, including the accumulation of dust in each detector. The analog information may also be used for automatic detector testing and the automatic determination of detector maintenance requirements.

J.	Addressable Charger Power Supply

1.	The auxiliary addressable power supply is a remote 24 VDC power supply used to power Notification Devices and field devices that require regulated 24 VDC power;  NOTIFIER model # ACPS-610

2.	The addressable power supply for the fire and gas detection system shall provide up to a minimum of 6.0 amps of 24 volt DC regulated power for Notification Appliance Circuit (NAC) power or 10.0 amps of 24 volt DC general power. The power supply shall have an additional 0.5 amp of 24 VDC auxiliary power for use within the same cabinet as the power supply. It shall include an integral charger designed to charge 12 - 200 amp hour batteries.

3.	The addressable power supply shall provide four individually addressable Notification Appliance Circuits that may be configured as  Class "A" or Class "B"  circuits. All circuits shall be power-limited per UL 864 requirements.

4.	The addressable power supply shall provide built-in synchronization for certain Notification Appliances on each circuit without the need for additional synchronization modules. The power supply's output circuits shall be individually selected for synchronization. A single addressable power supply shall be capable of supporting both synchronized and non-synchronized Notification Devices at the same time.

5.	The addressable power supply shall operate on 120 or 240 VAC, 50/60 Hz.

6.	The interface to the power supply from the Fire Alarm Control Panel (FACP) shall be via the Signaling Line Circuit (SLC) or other multiplexed means Power supplies that do not use an intelligent interface are not suitable substitutes. The required wiring from the FACP to the addressable power supply shall be a single unshielded twisted pair wire.

7.	The addressable power supply shall supervise for battery charging failure, AC power loss, power brownout, battery failure, NAC loss, and optional ground fault detection. In the event of a trouble condition, the addressable power supply shall report the incident and the applicable address to the FACP via the SLC.

8.	The addressable power supply shall have an AC Power Loss Delay option. If this option is utilized and the addressable power supply experiences an AC power loss, reporting of the incident to the FACP will be delayed. A delay time of zero, two, eight or sixteen hours shall be programmable.

9.	The addressable power supply shall have an option for Canadian Trouble Reporting and this option shall be programmable.

10.	The addressable power supply mounts in either the FACP backbox or it's own dedicated surface mounted backbox with cover.

11.	Each of the power supply's four output circuits shall be programmed- for Notification Appliance Circuit or General Purpose 24 VDC power. Any output circuit shall be able to provide up to 2.5 amps of 24 VDC power.

12.	The addressable power supply's output circuits shall be individually supervised when they are selected to be either a Notification Appliance Circuit when wired Class "A" or by the use of and end-of-line resistor. When the power supply's output circuit is selected as General 24 VDC power, the circuit shall be individually supervised when an end-of-line relay is used.

13.	When selected for Notification Appliance Circuits, the output circuits shall be individually programmable for Steady, March Time, Dual Stage or Temporal.

14.	When selected as a Notification Appliance Circuit, the output circuits of the addressable power supply shall have the option to be coded by the use of a universal zone coder.

15.	The addressable power supply shall interface and synchronize with other power supplies of the same type. The required wiring to interface multiple addressable power supplies shall be a single unshielded, twisted pair wire.

16.	An individual or multiple interfaced addressable power supplies shall have the option to use an external charger for battery charging. Interfaced power supplies shall have the option to share backup battery power.

K.	Remote Transmissions:

1.	Provide local energy or polarity reversal or trip circuits as required.

2.	The system shall be capable of operating a polarity reversal or local energy or fire alarm transmitter for automatically transmitting fire information to the fire department.

3.	Provide capability and equipment for transmission of zone alarm and trouble signals to remote operator's terminals, system printers and annunciators.

4.	Transmitters shall be compatible with the systems and equipment they are connected to such as timing, operation and other required features.

L.	Field Programming

1.	The system shall be programmable, configurable and expandable in the field without the need for special tools, laptop computers, or other electronic interface equipment. There shall be no firmware changes required to field modify the system time, point information, equations, or annunciator programming/information.

2.	It shall be possible to program through the standard FACP keyboard all system functions.

3.	All field defined programs shall be stored in non-volatile memory.

4.	Two levels of password protection shall be provided in addition to a key-lock cabinet. One level shall be used for status level changes such as point/zone disable or manual on/off commands (Building Manager). A second (higher-level) shall be used for actual change of the life safety program (installer). These passwords shall be five (5) digits at a minimum. Upon entry of an invalid password for the third time within a one minute time period an encrypted number shall be displayed. This number can be used as a reference for determining a forgotten password.

5.	The system programming shall be "backed" up via an upload/download program, and stored on compatible removable media. A system back-up disk shall be completed and given in duplicate to the building owner and/or operator upon completion of the final inspection. The program that performs this function shall be "non-proprietary", in that, it shall be possible to forward it to the building owner/operator upon his or her request.

6.	The installer's field programming and hardware shall be functionally tested on a computer against known parameters/norms which are established by the FACP manufacturer. A software program shall test Input-to-Output correlations, device Type ID associations, point associations, time equations, etc.  This test shall be performed on an IBM-compatible PC with a verification software package.  A report shall be generated of the test results and two copies turned in to the engineer(s) on record.

M.	Specific System Operations

1.	Smoke Detector Sensitivity Adjust: A means shall be provided for adjusting the sensitivity of any or all addressable intelligent detectors in the system from the system keypad. Sensitivity range shall be within the allowed UL window and have a minimum of 9 levels.

2.	Alarm Verification: Each of the intelligent addressable smoke detectors in the system may be independently selected and enabled to be an alarm verified detector. The alarm verification delay shall be programmable from 0 to 60 seconds and each detector shall be able to be selected for verification. The FACP shall keep a count of the number of times that each detector has entered the verification cycle. These counters may be displayed and reset by the proper operator commands.

N.	System Point Operations:

1.	Any addressable device in the system shall have the capability to be enabled or disabled through the system keypad or video terminal.

2.	System output points shall be capable of being turned on or off from the system keypad or the video terminal.

3.	Point Read: The system shall be able to display the following point status diagnostic functions without the need for peripheral equipment. Each point shall be annunciated for the parameters listed:

a.	Device Status.

b.	Device Type.

c.	Custom Device Label.

d.	Software Zone Label.

e.	Device Zone Assignments.

f.	Analog Detector Sensitivity.

g.	All Program Parameters.

4.	System History Recording and Reporting: The fire alarm control panel shall contain a history buffer that will be capable of storing up to 4000 system events. Each of these events will be stored, with time and date stamp, until an operator requests that the contents be either displayed or printed. The contents of the history buffer may be manually reviewed; one event at a time, and the actual number of activations may also be displayed and or printed.  History events shall include all alarms, troubles, operator actions, and programming entries.

5.	The history buffer shall use non-volatile memory. Systems which use volatile memory for history storage are not acceptable.

6.	Automatic Detector Maintenance Alert: The fire alarm control panel shall automatically interrogate each intelligent system detector and shall analyze the detector responses over a period of time.

7.	If any intelligent detector in the system responds with a reading that is below or above normal limits, then the system will enter the trouble mode, and the particular Intelligent Detector will be annunciated on the system display, and printed on the optional system printer. This feature shall in no way inhibit the receipt of alarm conditions in the system, nor shall it require any special hardware, special tools or computer expertise to perform.

8.	The system shall include the ability (programmable) to indicate a "pre-alarm" condition. This will be used to alert maintenance personal when a detector is at 80% of its alarm threshold in a 60 second period.

- System Maintenance Analysis and Reporting

- The system shall automatically track NFPA 72 installation and testing requirements for all addressable devices to ensure that every device is functionally tested upon installation and then periodically as required by the Code.

- If after twelve months any device has not been functionally tested a led shall illuminate on the CPU or Network annunciator indicating the device that needs testing.

- The system shall automatically track device testing to ensure that a visual inspection is performed at least semi-annually.

- If after six months a device has not been indicated as "visually inspected" a led shall illuminate on the CPU or Network annunciator indicating the device that needs testing.

- A hand-held IR tool may be used to interact with each SLC device to indicate that a visual inspection has been performed.  The IR device will explicitly identify the device by loop and address to ensure the correct visual inspection has been performed.

- A comprehensive report shall be available from the laptop programmer which shows a predictive report of all devices that have upcoming testing requirements.  These reports shall be configurable as either 30, 60 or 90 day predictive, current status, and "all database."

- Systems that do not automatically track the individual testing requirements of the field devices will not be accepted.

2.3	SYSTEM COMPONENTS:

A.	Conventional Aspirating Detection

1.	An optional air aspiration detection system shall be available.

2.	The aspirating system shall support multiple sensitivity settings.

3.	The aspirating system shall operate from 24 VDC.

4.	The aspirating system shall provide alarm and trouble relays used to activate a fire alarm control panel.

B.	Aspiration System Interface:

1.	The system shall be capable of supporting Interface Modules for integrating Vesda Aspiration detectors into SLC loop of the fire alarm control panel. The Interface Module shall support up to 19 detectors detectors, each SLC loop shall support one interface module.

C.	High Level Aspiration System Interface:

1.	The system shall be capable of supporting a High Level Interface for Vesda Aspirating Detection Systems.  The interface shall support up to 100 detectors and allow the fire alarm network to monitor and control events on the aspiration system.

D.	Communicators

1.	The UDACT shall be compact in size, mounting in a standard module position of the fire alarm control cabinet. Optionally, the UDACT shall have the ability for remote mounting, up to 6,000 feet from the fire alarm control panel. The wire connections between the UDACT and the control panel shall be supervised with one pair for power and one pair for multiplexed communication of overall system status.  Systems that utilize relay contact closures are not acceptable.

2.	The UDACT shall include connections for dual telephone lines (with voltage detect), per UL/NFPA/FCC requirements. It shall include the ability for split reporting of panel events up to two different telephone numbers.

3.	The UDACT shall be capable of transmitting events in 4+2, SIA, and Contact ID.

4.	Communication shall include vital system status such as:

a.	Independent Zone (Alarm, trouble, non-alarm, supervisory)

b.	Independent Addressable Device Status

c.	AC (Mains) Power Loss

d.	Low Battery and Earth Fault

e.	System Off Normal

f.	12 and 24 Hour Test Signal

g.	Abnormal Test Signal (per UL requirements)

h.	EIA-485 Communications Failure

i.	Phone Line Failure

5.	The UDACT shall support independent zone/point reporting when used in the Contact ID format. In this format the UDACT shall support transmission of up to 3,064 points. This enables the central station to have exact details concerning the origin of the fire or response emergency.

6.	The UDACT shall be capable of being programmed with the same programming utility as the host FACP, and saved, edited and uploaded and downloaded using the utility.  UDACT shall be capable of being programmed online or offline.  The programming utility shall also support upgrading UDACT operating firmware.

7.	The UDACT shall be capable of generating Central Station reports providing detailed programming information for each point along with the central station point address.

8.	An IP or IP/GSM Communicator option shall be available to interface to the UDACT and be capable of transmitting signals over the internet/intranet or Cellular (GSM) network to a compatible receiver.

2.4	Gateway & Webserver Options

A.	Common Alerting Protocol (CAP) Gateway: The system shall support an optional CAP Gateway (Common Alerting Protocol).  The CAP Gateway translates fire system messages to industry standard CAP messages for integration with CAP-compliant clients. A CAP gateway shall be available from the fire alarm control panel manufacturer.

B.	LEDSIGN Gateway: The system shall support an optional and proprietary LEDSIGN Gateway to interface to LED signs that will automatically display emergency messages.  The signs shall be capable of storing up to 100 messages that can be activated via system programming with the ability to be manually overridden.  The Sign Gateway shall support up to 10 independent signs, each sign capable of playing an independent message.  Multiple LEDSIGN Gateways can be used in network applications. An LEDSIGN gateway shall be available from the fire alarm control panel manufacturer.

C.	BACnet Interface Gateway: The system shall be capable of being interfaced with BACNet compliant clients. A BACnet interface supporting BACnet/IP communication shall be available from the fire alarm control panel manufacturer.

D.	MODbus Interface Gateway: The system shall be capable of being interfaced with MODbus compliant clients. A MODbus interface supporting MODbus/TCP communication shall be available from the fire alarm control panel manufacturer.

E.	Noti-Fire-Net Gateway: The system shall support an IP based gateway to enable the panel or local Noti-Fire-Net to be connected to an ONYXWorks workstation via the Internet or Intranet. This gateway shall also support the ability to integrate the system to an interactive firefighter’s display. The Noti-Fire-Net Gateway shall be available from  the fire alarm control manufacturer.

F.	Webserver:  The system shall support a webserver allowing remote connection via the Internet or Intranet. Authorized users will have the ability to view panel/network history, event status and device properties.  The webserver shall also support sending event information via email or text to up to 50 registered users, the webserver shall be available from the fire alarm control panel manufacturer.

G.	Web Portal Interface:  The system shall be capable of being interfaced with a web portal to integrate with Inspection and Service Manager utilities.  The web portal and inspection and service manager utilities shall be available from the fire alarm control panel manufacturer.

2.5	SYSTEM COMPONENTS - ADDRESSABLE DEVICES

A.	Addressable Devices - General

1.	Addressable devices shall provide an address-setting means using rotary decimal switches.  Addressable devices that require the address be programmed using a programming utility are not an allowable substitute .

Addressable devices shall use simple to install and maintain decade, decimal address switches. Devices shall be capable of being set to an address in a range of 001 to 159.

2.	Addressable devices, which use a binary-coded address setting method, such as a DIP-switch, are not an allowable substitute. Addressable devices that require the address be programmed using a special tool or programming utility are not an allowable substitute.

3.	Detectors shall be intelligent (analog) and addressable, and shall connect with two wires to the fire alarm control panel Signaling Line Circuits.

4.	Addressable smoke and thermal detectors shall provide dual alarm and power/polling LEDs. Both LEDs shall flash green under normal conditions, indicating that the detector is operational and in regular communication with the control panel, and both LEDs shall be placed into steady red illumination by the control panel, indicating that an alarm condition has been detected. If required, the LED flash shall have the ability to be removed from the system program. An output connection shall also be provided in the base to connect an external remote alarm LED.

5.	The fire alarm control panel shall permit detector sensitivity adjustment through field programming of the system. The panel on a time-of-day basis shall automatically adjust sensitivity.

6.	Using software in the FACP, detectors shall automatically compensate for dust accumulation and other slow environmental changes that may affect their performance. The detectors shall be listed by UL as meeting the calibrated sensitivity test requirements of NFPA Standard 72.

7.	The detectors shall be ceiling-mount and shall include a separate twist-lock base with tamper proof feature. Base options shall include a sounder base with a built-in (local) sounder rated at 85 DBA minimum, a relay base and an isolator base designed for Style 7 applications. The system shall also support an intelligent programmable sounder base, the programmable sounder base shall be capable of providing multiple tones based on programming and at a minimum be capable of providing a Temp-4 tone for CO (Carbon Monoxide) activation and a Temp-3 tone for fire activations and be capable of being synchronized with other programmable sounder bases and common area notification appliances; 85 DBA minimum.

8.	Detectors shall also store an internal identifying type code that the control panel shall use to identify the type of device (ION, PHOTO, THERMAL).

9.	Detectors will operate in an analog fashion, where the detector simply measures its designed environment variable and transmits an analog value to the FACP based on real-time measured values. The FACP software, not the detector, shall make the alarm/normal decision, thereby allowing the sensitivity of each detector to be set in the FACP program and allowing the system operator to view the current analog value of each detector.

10.	Addressable devices shall store an internal identifying code that the control panel shall use to identify the type of device.

11.	A magnetic test switch shall be provided to test detectors and modules. Detectors shall report an indication of an analog value reaching 100% of the alarm threshold.

12.	Addressable modules shall mount in a 4-inch square (101.6 mm square), 2-1/8 inch (54 mm) deep electrical box. An optional surface mount Lexan enclosure shall be available.

B.	Addressable Manual Fire Alarm Box (manual station)

1.	Addressable manual fire alarm boxes shall, on command from the control panel, send data to the panel representing the state of the manual switch and the addressable communication module status; NOTIFIER model # NBG-12LX. They shall use a key operated test-reset lock, and shall be designed so that after actual emergency operation, they cannot be restored to normal use except by the use of a key.

2.	All operated stations shall have a positive, visual indication of operation and utilize a key type reset.

3.	Manual fire alarm boxes shall be constructed of Lexan with clearly visible operating instructions provided on the cover. The word FIRE shall appear on the front of the stations in raised letters, 1.75 inches (44 mm) or larger.

C.	Intelligent Photoelectric Smoke Detector: The intelligent photoelectric smoke detector shall be NOTIFIER model # FSP-851 and shall use the photoelectric (light-scattering) principal to measure smoke density and shall, on command from the control panel, send data to the panel representing the analog level of smoke density.

D.	Intelligent VIEW® Laser Photo Smoke Detector: The intelligent laser photo smoke detector shall be a spot type detector, NOTIFIER model # FSL-751, that incorporates an extremely bright laser diode and an integral lens that focuses the light beam to a very small volume near a receiving photo sensor. The scattering of smoke particles shall activate the photo sensor.

1.	The laser detector shall have conductive plastic so that dust accumulation is reduced significantly.

2.	The intelligent laser photo detector shall have nine sensitivity levels and be sensitive to a minimum obscuration of 0.02 percent per foot.

3.	The laser detector shall not require expensive conduit, special fittings or PVC pipe.

4.	The intelligent laser photo detector shall support standard, relay, isolator and sounder detector bases.

5.	The laser photo detector shall not require other cleaning requirements than those listed in NFPA 72. Replacement, refurbishment or specialized cleaning of the detector head shall not be required.

6.	The laser photo detector shall include two bicolor LEDs that flash green in normal operation and turn on steady red in alarm.

E.	Intelligent Ionization Smoke Detector: The intelligent ionization smoke detector shall be NOTIFIER model # FSI-851 and shall use the dual-chamber ionization principal to measure products of combustion and shall, on command from the control panel, send data to the panel representing the analog level of products of combustion.

F.	Intelligent Multi Criteria Acclimating Detector: The intelligent multi-criteria Acclimate® Plus™ detector shall be an addressable device, NOTIFIER model # FAPT-851, that is designed to monitor a minimum of photoelectric and thermal technologies in a single sensing device. The design shall include the ability to adapt to its environment by utilizing a built-in microprocessor to determine its environment and choose the appropriate sensing settings. The detector design shall allow a wide sensitivity window, no less than 1 to 4% per foot obscuration. This detector shall utilize advanced electronics that react to slow smoldering fires and thermal properties all within a single sensing device.

1.	The microprocessor design shall be capable of selecting the appropriate sensitivity levels based on the environment type it is in (office, manufacturing, kitchen etc.) and then have the ability to automatically change the setting as the environment changes (as walls are moved or as the occupancy changes).

2.	The intelligent multi criteria detection device shall include the ability to combine the signal of the thermal sensor with the signal of the photoelectric signal in an effort to react hastily in the event of a fire situation. It shall also include the inherent ability to distinguish between a fire condition and a false alarm condition by examining the characteristics of the thermal and smoke sensing chambers and comparing them to a database of actual fire and deceptive phenomena.

G.	Intelligent Thermal Detectors: The intelligent thermal detectors shall be NOTIFIER FST- series addressable devices rated at 135 degrees Fahrenheit (58 degrees Celsius) and have a rate-of-rise element rated at 15 degrees F (9.4 degrees C) per minute.  A high heat thermal detector rated at 190 degrees Fahrenheit shall also be available.  The thermal detectors shall connect via two wires to the fire alarm control panel signaling line circuit.

H.	Intelligent Duct Smoke Detector: The smoke detector housing shall accommodate an intelligent photoelectric detector that provides continuous analog monitoring and alarm verification from the panel.  When sufficient smoke is sensed, an alarm signal is initiated at the FACP, and appropriate action taken to change over air handling systems to help prevent the rapid distribution of toxic smoke and fire gases throughout the areas served by the duct system.  The Intelligent Duct Smoke Detector shall support the installation of addressable Photoelectric detector capable or being tested remotely.  The Intelligent Duct Detector housing shall be model # DNR(W) and the remote test capable photoelectric smoke detector shall be NOTIFIER model # FSP-851R.

I.	IntelliQuad™ Advanced Multi-Criteria Intelligent Detector

1.	Intelligent multi-criteria fire detector shall be a NOTIFIER model number FSC-851.  Smoke detector shall be an addressable intelligent multi-criteria smoke detector. The detector shall be comprised of four sensing elements, including a photoelectric (light-scattering) particulate sensor, an electrochemical carbon monoxide (CO) sensor, a daylight-filtered infrared sensor and solid state thermal sensor(s) rated at 135°F (57.2°C).   The device shall be able to indicate distinct smoke and heat alarms.

2.	The intelligent multi-criteria detection device shall include the ability to combine the signal of the photoelectric signal with other sensing elements in an effort to react quickly in the event of a fire situation.  It shall also include the inherent ability to distinguish between a fire condition and a nuisance alarm condition.  The product design shall be capable of selecting the appropriate sensitivity levels based on the environment type chosen by user in which it is installed (office, manufacturing, kitchen etc.) and then have the ability to automatically change the setting as the environment changes.

3.	The detector shall be capable of automatically adjusting its sensitivity by means of drift compensation and smoothing algorithms.  The detector shall be capable of automatically adjusting its sensitivity by means of drift compensation and smoothing algorithms.  The device shall provide unique signals to indicate when 20% of the drift range is remaining, when 100% of drift range is used, and when there is a chamber fault to show unit requires maintenance.

4.	The detector shall indicate CO trouble conditions including 6 months of sensor life remaining and sensor life has expired.  The detector shall indicate a combined signal for any of the following:  low chamber trouble, thermistor trouble, CO self test failure, IR self test failure, and freeze warning.

5.	The detectors shall provide address-setting means on the detector head using rotary switches.  Because of the possibility of installation error, systems that use binary jumpers or DIP switches to set the detector address are not acceptable.  The detectors shall also store an internal identifying code that the control panel shall use to identify the type of detector.  Systems that require a special programmer to set the detector address (including temporary connection at the panel) are labor intensive and not acceptable. Each detector occupies any one of at least 99 possible addresses on the signaling line circuit (SLC) loop.  It responds to regular polls from the system and reports its type and status.

6.	The detectors shall provide a test means whereby they will simulate an alarm condition and report that condition to the control panel. Such a test may be initiated at the detector itself (by activating a switch) or initiated remotely on command from the control panel.  There are three test methods:  functional magnet, smoke entry aerosol, or direct heat method.

7.	The detectors shall provide two LEDs to provide 360° visibility.  The LEDs are placed into steady red illumination by the control panel indicating that an alarm condition has been detected.  An output connection shall also be provided in the base to connect an external remote alarm LED, sounder base, and / or relay base (optional accessories).  The external remote alarm can be interconnected to other sounder or relay bases for activating all devices in a space via a single alarming unit.

8.	Two LEDs on the sensor are controlled by the panel to indicate sensor status. Coded signals, transmitted from the panel, can cause the LEDs to blink, latch on, or latch off. Refer to the control panel technical documentation for sensor LED status operation and expected delay to alarm.

9.	The detectors shall be ceiling-mount and shall be plug-in mounted into a twist-lock base.   These detectors shall be constructed of off-white UV resistant polymer and shall be detachable from the mounting base to simplify installation, service and maintenance. Mounting base wiring connections shall be made by means of SEMS screws. The detector shall allow pre-wiring of the base and the head shall be a plug-in type.   Mounting base shall be mounted on junction box which is at least 1.5 inches (3.81 cm) deep. Mounting base shall be available to mount to standard junction boxes.  Suitable boxes include:

a.	4.0" (10.16 cm) square box with and without plaster ring.

b.	4.0" (10.16 cm) octagonal box.

c.	3.5" (8.89 cm) octagonal box.

d.	Single-gang box.

10.	Meets Agency Standards

a.	ANSI/UL 268 -Smoke Detectors for Fire Alarm Signaling Systems

b.	CAN/ULC-S529- Smoke Detectors for Fire Alarm Systems

c.	FM 3230-3250- Smoke Actuated Detectors for Automatic Fire Alarm Signaling

J.	IntelliQuad™ PLUS Advanced Multi-Criteria Intelligent Fire/CO Detector

1.	Advanced Multi-Criteria Fire/CO detector shall be NOTIFIER model # FCO-851 and shall be an addressable advanced multi-criteria smoke detector with a separate signal for carbon monoxide (CO) detection per UL 2075 standards.

2.	The detector shall be comprised of four sensing elements, including a photoelectric (light-scattering) particulate sensor, an electrochemical CO sensor, a daylight-filtered infrared (IR) sensor and solid state thermal sensor(s) rated at 135°F (57.2°C). The device shall be able to indicate distinct smoke and heat alarms.

3.	The advanced multi-criteria detection device shall include the ability to combine the signal of the photoelectric signal with other sensing elements in order to react quickly in the event of a fire situation. It shall also include the inherent ability to distinguish between a fire condition and a nuisance alarm condition. The detector shall be capable of selecting the appropriate sensitivity levels based on the environment type (office, manufacturing, kitchen, etc.) in which it is installed, and then have the ability to automatically change the setting as the environment changes.

4.	The CO detector component shall be capable of a functional gas test using a canned test agent to test the functionality of the CO sensing cell.

5.	The detector shall be capable of automatically adjusting its sensitivity by means of drift compensation and smoothing algorithms. The device shall provide unique signals to indicate when 20 percent of the drift range is remaining, when 100 percent of drift range is used, and when there is a chamber fault to show the unit requires maintenance.

6.	The detector shall indicate CO trouble conditions, including six months of sensor life remaining and sensor life has expired. The detector shall indicate a combined signal for any of the following: low chamber trouble, thermistor trouble, CO self test failure, IR self test failure, and freeze warning.

7.	The detector shall provide address-setting means on the detector head using rotary switches. Because of the possibility of installation error, systems that use binary jumpers or DIP switches to set the detector address are not acceptable. The detector shall also store an internal identifying code that the control panel shall use to identify the type of detector. Systems that require a special programmer to set the detector address (including temporary connection at the panel) are labor intensive and not acceptable. Each detector occupies any one of at least 159 possible addresses on the signaling line circuit (SLC) loop. It responds to regular polls from the system and reports its type and status.

8.	The detector shall provide a test means whereby it will simulate an alarm condition and report that condition to the control panel. Such a test may be initiated at the detector itself (by activating a switch) or initiated remotely on command from the control panel. There shall be four test methods: functional magnet, smoke entry aerosol, carbon monoxide aerosol or direct heat method.

9.	The detector shall provide two LEDs to provide 360° visibility. The LEDs shall be placed into steady red illumination by the control panel indicating that an alarm condition has been detected. An output connection shall also be provided in the base to connect an external remote alarm LED. The detector must be capable of connecting to a sounder base that provides both temporal 3 and temporal 4 patterns for fire and CO alarm.

10.	Two LEDs on the sensor shall be controlled by the panel to indicate sensor status. Coded signals, transmitted from the panel, shall cause the LEDs to blink, latch on, or latch off. Refer to the control panel technical documentation for sensor LED status operation and expected delay to alarm.

11.	The detector shall be plug-in mounted into a twist-lock base. The detector shall be constructed of off-white, UV-resistant polymer and shall be detachable from the mounting base to simplify installation, service and maintenance. Mounting base wiring connections shall be made by means of SEMS screws. The detector shall allow pre-wiring of the base and the head shall be a plug-in type. The mounting base shall be mounted on a junction box that is at least 1.5 inches (3.81 cm) deep. The mounting base shall be available to mount to standard junction boxes.  Suitable boxes include:

a.	4.0" (10.16 cm) square box with and without plaster ring.

b.	4.0" (10.16 cm) octagonal box.

c.	3.5" (8.89 cm) octagonal box.

d.	Single-gang box.

e.	Double-gang box

12.	Meets Agency Standards

a.	ANSI/UL 268 -Smoke Detectors for Fire Alarm Signaling Systems

b.	CAN/ULC-S529- Smoke Detectors for Fire Alarm Systems

c.	FM 3230-3250- Smoke Actuated Detectors for Automatic Fire Alarm Signaling

d.	UL 2075 – Gas and Vapor Detector and Sensors – Systems Connected

K.	Intelligent Addressable Aspiration Detector: The intelligent aspiration detector shall be NOTIFIER model # FSA-8000 an addressable aspiration detector that communicates directly with the fire alarm control panel via the SLC communication protocol, no modules or high level interfaces shall be required. The fire alarm control panel shall support up to thirty one intelligent aspiration detectors per SLC loop. The aspiration detector shall have dual source (blue LED and infra-red laser) optical smoke detection for a wide range of fire detection with enhanced immunity to nuisance particulates. The FACP shall be capable of monitoring and annunciating up to five smoke event thresholds and eleven trouble conditions.  Each event threshold shall be capable of being assigned a discrete type ID at the FACP

L.	Intelligent Addressable Reflected Beam Detector

1.	The intelligent single-ended reflected beam smoke detector shall connect with two wires to the fire alarm control panel signaling line circuit (SLC).  The detectors shall consist of a transmitter/receiver unit and a reflector and shall send data to the panel representing the analog level of smoke density. The detector shall be capable of being tested remotely via a keyswitch; NOTIFIER model # FSB-200.  Model # FSB-200S shall be equipped with an integral sensitivity test feature.

M.	Addressable Dry Contact Monitor Module

1.	Addressable monitor modules shall be provided to connect one supervised IDC zone of conventional alarm initiating devices (any N.O. dry contact device) to one of the fire alarm control panel SLCs.  The addressable monitor module shall be NOTIFIER model # FMM-1 (Class A or B) or FMM-101 (Class B)

2.	The IDC zone shall be suitable for Style D/Class A or Style B/Class B operation. An LED shall be provided that shall flash under normal conditions, indicating that the monitor module is operational and in regular communication with the control panel.

3.	For difficult to reach areas, the monitor module shall be available in a miniature package and shall be no larger than 2-3/4 inch (70 mm) x 1-1/4 inch (31.7 mm) x 1/2 inch (12.7 mm). This version need not include Style D or an LED.

4.	For multiple dry contact monitoring a module shall be available that provides 10 Style B or 5 Style D input circuits; NOTIFIER model # XP10-M.

N.	Two Wire Detector Monitor Module

1.	Addressable monitor modules shall be provided to connect one supervised IDC zone of conventional 2-wire smoke detectors or alarm initiating devices (any N.O. dry contact device); NOTIFIER model # FZM-1.

2.	The IDC zone may be wired for Class A or B (Style D or Style B) operation. An LED shall be provided that shall flash under normal conditions, indicating that the monitor module is operational and in regular communication with the control panel.

3.	For multiple 2-wire smoke detector circuit monitoring a module shall be available that provides 6 Style B/Class A or 3 Style D/Class B input circuits; NOTIFIER model # XP6-MA.

O.	Addressable Control Module

1.	Addressable control modules shall be provided to supervise and control the operation of one conventional circuit of compatible Notification Appliances, 24 VDC powered, polarized audio/visual notification appliances; NOTIFIER model # FCM-1

2.	The control module NAC may be wired for Style Z or Style Y (Class A/B) with a current rating of 2 Amps for Style Z and 3 Amps for Style Y;

3.	Audio/visual power shall be provided by a separate supervised circuit from the main fire alarm control panel or from a supervised UL listed remote supply.

4.	For multiple circuit control a module shall be available that provides 6 Style Y (Class B) or 3 Style Z (Class A) control circuits; NOTIFIER model # XP6-C.

P.	Addressable Releasing Control Module

1.	An addressable FlashScan releasing module shall be available to supervise and control compatible releasing agent solenoids; NOTIFIER model # FCM-1-REL.

2.	The module shall operate on a redundant protocol for added protection.

3.	The module shall be configurable for Style Z or Style Y (Class  A/B) and support one 24 volt or two 12 volt solenoids.

Q.	Addressable 4-20 mA Module

1.	Addressable 4-20 mA module shall be available to monitor industry-standard, linear-scale, 4-20 mA protocol sensors. The module converts the sensor output to communication protocol that can be interpreted by the FACP for monitoring and display; NOTIFIER model # FMM-4-20

2.	The module shall support programming of up to five programmable event thresholds.

3.	The System shall be FM 6320 (Factory Mutual) approved as a Gas Detection system when employed with the FMM-4-20 monitor module and industry standard 4-20 mA gas detectors.

R.	Addressable Relay Module:

1.	Addressable Relay Modules shall be available for HVAC control and other network building functions; NOTIFIER model # FRM-1.

2.	The module shall provide two form C relays rated at up to 3 Amps resistive and up to 2.0 Amps inductive.

3.	The relay coil shall be magnetically latched to reduce wiring connection requirements, and to insure that 100% of all auxiliary devices energize at the same time on the same pair of wires.

4.	For multiple relay control a module shall be available that provides 6 programmable Form-C relays; NOTIFIER model # XP6-R.

S.	Addressable Two-In / Two-Out Monitor/Relay Module:

1.	An addressable Two-In / Two-Out module shall be available; NOTIFIER model # FDRM-1.

2.	The two-in/two-out module shall provide two Class B/Style B dry-contact input circuits and two independent Form-C relays rated at up to 3 Amps resistive and up to 2.0 Amps inductive.

T.	Isolator Module: Isolator modules shall be provided to automatically isolate wire-to-wire short circuits on an SLC Class A or Class B branch. The isolator module shall limit the number of modules or detectors that may be rendered inoperative by a short circuit fault on the SLC loop segment or branch. At least one isolator module shall be provided for each floor or protected zone of the building; NOTIFIER model # ISO-X.

1.	If a wire-to-wire short occurs, the isolator module shall automatically open-circuit (disconnect) the SLC. When the short circuit condition is corrected, the isolator module shall automatically reconnect the isolated section.

2.	The isolator module shall not require address-setting, and its operations shall be totally automatic. It shall not be necessary to replace or reset an isolator module after its normal operation.

3.	The isolator module shall provide a single LED that shall flash to indicate that the isolator is operational and shall illuminate steadily to indicate that a short circuit condition has been detected and isolated.

U.	Smoke Control Annunciator

1.	On/Auto/Off switches and status indicators (LEDS) shall be provided for monitoring and manual control of each fan, damper, HVAC control unit, stairwell pressurization fan, and smoke exhaust fan. To ensure compliance the units supplied shall meet the following UL categories: UUKL, PAZX, UDTZ, QVAX as well as the requirements of NFPA 90A, HVAC, and NFPA 92A & 92B, Smoke Control. The control System shall be field programmable for either 90A operation or 92A/B operation to allow for future use and system expansion.

2.	The OFF LED shall be Yellow, the ON LED shall be green, the Trouble/Fault LED shall be Amber/Orange for each switch. The Trouble/Fault indicator shall indicate a trouble in the control and/or monitor points associated with that switch. In addition, each group of eight switches shall have two LEDS and one momentary switch which allow the following functions: An Amber LED to indicate an OFF-NORMAL switch position, in the ON or OFF position; A Green LED to indicate ALL AUTO switch position; A Local Acknowledge/Lamp Test momentary switch.

3.	Each switch shall have the capability to monitor and control two addressable inputs and two addressable outputs. In all modes, the ON and OFF indicators shall continuously follow the device status not the switch position. Positive feedback shall be employed to verify correct operation of the device being controlled. Systems that indicate on/off/auto by physical switch position only are not acceptable.

4.	All HVAC switches (i.e., limit switches, vane switches, etc.) shall be provided and installed by the HVAC contractor.

5.	It shall be possible to meet the requirements mentioned above utilizing wall mounted custom graphic.

V.	Serially Connected Annunciator Requirements

1.	The annunciator shall communicate to the fire alarm control panel via an EIA 485 (multi-drop) two-wire communications loop. The system shall support two 6,000 ft. EIA-485 wire runs. Up to 32 annunciators, each configured up to 96 points, may be connected to the connection, for a system capacity of 3,072 points of annunciation.

2.	An EIA-485 repeater shall be available to extend the EIA-485 wire distance in 3,000 ft. increments. . The repeater shall be UL864 approved.

3.	Each annunciator shall provide up to 96 alarm and 97 trouble indications using a long-life programmable color LED's. Up to 96 control switches shall also be available for the control of Fire Alarm Control Panel functions. The annunciator will also have an "ON-LINE" LED, local piezo sounder, local acknowledge and lamp test switch, and custom zone/function identification labels.

4.	The annunciator may be field configured to operate as a "Fan Control Annunciator". When configured as "Fan Control," the annunciator may be used to manually control fan or damper operation and can be set to override automatic commands to all fans/dampers programmed to the annunciator.

5.	Annunciator switches may be programmed for System control such as, Global Acknowledge, Global Signal Silence, Global System Reset, and on/off control of any control point in the system.

6.	An optional module shall be available to utilize annunciator points to drive EIA-485 driven relays. This shall extend the system point capacity by 3,072 remote contacts.

7.	The LED annunciator shall offer an interface to a graphic style annunciator and provide each of the features listed above.

W.	SpectrAlert Advance Speakers

1.	The Speaker appliance shall be System Sensor SpectrAlert Advance model ______ Speaker. The speaker shall be listed to UL 1480 for Fire Protective Signaling Systems. It shall be a dual-voltage transformer speaker capable of operation at 25.0 or 70.7 nominal Vrms. The speaker shall have a frequency range of 400 to 4,000 Hz and shall have an operating temperature between 32°F and 120°F. It shall mount to a 4 x 4 x 2 1/8-inch back box.

2.	A universal mounting plate shall be used for mounting ceiling and wall speaker products. The notification appliance circuit and amplifier wiring shall terminate at the universal mounting plate.

3.	Speakers shall be plug-in and shall have the ability to check wiring continuity via a shorting spring on the universal mounting plate. The shorting spring shall also provide tamper resistance via an open circuit if the device is removed. Speaker design shall isolate speaker components to reduce ground fault incidents.

4.	The speaker shall have power taps (from ¼ watt to 2 watts) and voltage that are selected by rotary switches. All models shall have a maximum sound output of 86 dB at 10 feet and shall incorporate an open back construction.

5.	All notification appliances shall be backward compatible.

Ceiling Speaker				  Wall Speaker

X.	SpectrAlert Advance Speaker Strobes

1.	The Speaker Strobe appliance shall be System Sensor SpectrAlert Advance model ______ Speaker Strobe. The speaker strobe shall be listed to UL 1971 and UL 1480 and be approved for fire protective signaling systems. It shall be a dual-voltage transformer speaker strobe capable of operation at 25.0 or 70.7 nominal Vrms. The speaker shall have a frequency range of 400 to 4,000 Hz and shall have an operating temperature between 32°F and 120°F. It shall mount to a 4 x 4 x 2 1/8-inch back box.

2.	A universal mounting plate shall be used for mounting ceiling and wall speaker strobe products. The notification appliance circuit and amplifier wiring shall terminate at the universal mounting plate.  Also, SpectrAlert Advance speaker strobes and the Sync•Circuit™ Module MDL3 accessory, if used, shall be powered from a non-coded notification appliance circuit output and shall operate on a nominal 12 or 24 volts (includes fire alarm panels with built in sync). When used with the Sync•Circuit Module MDL3, 12-volt rated notification appliance circuit outputs shall operate between 8.5 and 17.5 volts; 24-volt rated notification appliance circuit outputs shall operate between 16.5 to 33 volts. If the notification appliances are not UL 9th edition listed with the corresponding panel or power supply being used, then refer to the compatibility listing of the panel to determine maximum devices on a circuit.

3.	Speaker strobes shall be plug-in and shall have the ability to check wiring continuity via a shorting spring on the universal mounting plate. The shorting spring shall also provide tamper resistance via an open circuit if the device is removed. Speaker strobe design shall isolate speaker components to reduce ground fault incidents.

4.	The speaker strobe shall have power taps (from ¼ watt to 2 watts) and voltage that are selected by rotary switches. All models shall have a maximum sound output of 86 dB at 10 feet and shall incorporate an open back construction.  The strobe shall consist of a xenon flash tube with associated lens/reflector system and operate on either 12V or 24V. The strobe shall also feature selectable candela output, providing options for 15 or 15/75 candela when operating on 12V and 15, 15/75, 30, 75, 110, or 115 when operating on 24V. The strobe shall comply with NFPA 72 and the Americans with Disabilities Act requirement for visible signaling appliances, flashing at 1 Hz over the strobe’s entire operating voltage range.

5.	All notification appliances shall be backward compatible.

Ceiling Speaker Strobe		       Wall Speaker Strobe

6.	Strobe lights shall meet the requirements of the ADA, UL Standard 1971and be fully synchronized.

PART 3.0 - EXECUTION

3.1.	INSTALLATION:

A.	Installation shall be in accordance with the NEC, NFPA 72, local and state codes, as shown on the drawings, and as recommended by the major equipment manufacturer.

B.	All conduit, junction boxes, conduit supports and hangers shall be concealed in finished areas and may be exposed in unfinished areas. Smoke detectors shall not be installed prior to the system programming and test period. If construction is ongoing during this period, measures shall be taken to protect smoke detectors from contamination and physical damage.

C.	All fire detection and alarm system devices, control panels and remote annunciators shall be flush mounted when located in finished areas and may be surface mounted when located in unfinished areas.

D.	Manual fire alarm boxes shall be suitable for surface mounting or semi-flush mounting as shown on the plans, and shall be installed not less than 42 inches (1067 mm), nor more than 48 inches (122 mm) above the finished floor.

3.2.	TEST:

The service of a competent, factory-trained engineer or technician authorized by the manufacturer of the fire alarm equipment shall be provided to technically supervise and participate during all of the adjustments and tests for the system. All testing shall be in accordance with NFPA 72.

A.	Before energizing the cables and wires, check for correct connections and test for short circuits, ground faults, continuity, and insulation.

B.	Close each sprinkler system flow valve and verify proper supervisory alarm at the FACP.

C.	Verify activation of all waterflow switches.

D.	Open initiating device circuits and verify that the trouble signal actuates.

E.	Open and short signaling line circuits and verify that the trouble signal actuates.

F.	Open and short notification appliance circuits and verify that trouble signal actuates.

G.	Ground all circuits and verify response of trouble signals.

H.	Check presence and audibility of tone at all alarm notification devices.

I.	Check installation, supervision, and operation of all intelligent smoke detectors using the walk test.

J.	Each of the alarm conditions that the system is required to detect should be introduced on the system. Verify the proper receipt and the proper processing of the signal at the FACP and the correct activation of the control points.

K.	When the system is equipped with optional features, the manufacturer's manual shall be consulted to determine the proper testing procedures. This is intended to address such items as verifying controls performed by individually addressed or grouped devices, sensitivity monitoring, verification functionality and similar.

3.3.	FINAL INSPECTION:

A.	At the final inspection, a factory-trained representative of the manufacturer of the major equipment shall demonstrate that the system functions properly in every respect.

3.4.	INSTRUCTION:

A.	Instruction shall be provided as required for operating the system. Hands-on demonstrations of the operation of all system components and the entire system including program changes and functions shall be provided.

B.	The contractor and/or the systems manufacturer's representatives shall provide a typewritten "Sequence of Operation."

END OF SECTION