SECTION 13850 (28 31 00)

FIRE & GAS DETECTION AND ALARM SYSTEM

ENGINEERING SPECIFICATION

INTELLIGENT REPORTING FIRE & GAS DETECTION SYSTEM

PART 1	GENERAL

1.1	RELATED SECTIONS

A.	Section 13800 - Building Automation and Control.

B.	Section 13900 (21 00 00) - Fire Suppression.

C.	Section (27 15 00) - (Fire Alarm Communications Horizontal Cabling).

1.2	DESCRIPTION

A.	The fire alarm system shall comply with requirements of NFPA Standard 72 for Protected   Premises Signaling Systems except as modified and supplemented by this specification.  The system shall be electrically supervised and monitor the integrity of all conductors.

B.	The facility shall have an emergency voice alarm communication system.  Digitally stored message sequences shall notify the building occupants that a fire or life safety condition has been reported.  Message generator(s) shall be capable of automatically distributing up to eight (8) simultaneous, unique messages to appropriate audio zones within the facility based on the type and location of the initiating event.   The Fire Command Center (FCC) shall also support Emergency manual voice announcement capability for both system wide or selected audio zones, and shall include provisions for the system operator to override automatic messages system wide or in selected zones.

C.	The system shall be support additional, alternate Fire Command Centers, which shall be capable of simultaneous monitoring of all system events.  Alternate Fire Command Centers shall also support an approved method of transferring the control functions to an alternate Fire Command Center when necessary.  All Fire Command Centers shall be individually capable of assuming Audio Command functions such as Emergency Paging, audio zone control functions, and Firefighter's Telephone communication functions.

D.	Each designated zone shall transmit separate and different alarm, supervisory and trouble signals to the Fire Command Center (FCC) and designated personnel in other buildings at the site via a multiplex communication network.

E.	The fire alarm system shall be manufactured by an ISO 9001:2008 certified company and meet the requirements of BS EN9001: ANSI/ASQC Q9001-1994

F.	The FACP and peripheral devices shall be manufactured 100% by a single U.S. manufacturer (or division thereof).   It’s acceptable for peripheral devices to be manufactured outside of the U.S. by a division of the U.S. based parent company.

G.	The system and its components shall be Underwriters Laboratories, Inc. listed under the appropriate UL testing standard as listed herein for fire alarm applications and the installation shall be in compliance with the UL listing.

H.	The installing company shall employ NICET (minimum Level II Fire Alarm Technology) technicians on site to guide the final checkout and to ensure the systems integrity.

1.3	GUARANTY:

A.	The fire alarm control panel, voice panels and any head-end equipment shall have a manufacturer’s warranty of a minimum of 3 years.

1.4	POST CONTRACT MAINTENANCE:

A.	Complete maintenance and repair service for the fire and gas detection system shall be available from a factory trained authorized representative of the manufacturer of the major equipment for a period of five (5) years after expiration of the guaranty.

B.	As part of the bid/proposal, include a quote for a maintenance contract to provide all maintenance, required tests, and list pricing for any replacement products included on the bill of materials, along with the list pricing for products not on the bill of materials; if test and inspection rates are different than full service rates the bid/proposal shall include pricing for all levels for a minimum period of five (5) years  Rates and costs shall be valid for the period of five (5) years after expiration of the guaranty.

C.	Include also a quote for unscheduled maintenance/repairs, including hourly rates for technicians trained on this equipment, and response travel costs for each year of the maintenance period. Submittals that do not identify all post contract maintenance costs will not be accepted. Rates and costs shall be valid for the period of five (5) years after expiration of the guaranty.

1.5	APPLICABLE STANDARDS AND SPECIFICATIONS:

A.	The specifications and standards listed below form a part of this specification. The system shall fully comply with the latest issue of these standards, if applicable.

B.	National Fire Protection Association (NFPA) - USA:

| No. 12 | Extinguishing Systems (low and high) |
| --- | --- |
| No. 12A | Halon 1301 Extinguishing Systems |
| No. 13 | Sprinkler Systems |
| No. 15 | Water Spray Systems |
| No. 16 | Foam / Water Deluge and Spray Systems |
| No. 17 | Dry Chemical Extinguishing Systems |
| No. 17A | Wet Chemical Extinguishing Systems |
| No. 2001 | Clean Agent Extinguishing Systems |
| No. 70 | National Electric Code |
| No. 90A | Air Conditioning Systems |
| No. 92A | Smoke Control Systems |
| No. 92B | Smoke Management Systems in Malls, Atria, Large Areas |
| No. 72 | National Fire Alarm Code |
| No. 101 | Life Safety Code |

C.	Underwriters Laboratories Inc. (UL) - USA:

| No. 268 | Smoke Detectors for Fire Protective Signaling Systems |
| --- | --- |
| No. 864 | Control Units for Fire Protective Signaling Systems |
| No. 2572 | Mass Notification Systems |
| No. 217 | Smoke Detectors, Single and Multiple Station |
| No. 228 | Door Closers - Holders for Fire Protective Signaling Systems |
| No. 268A | Smoke Detectors for Duct Applications |
| No. 521 | Heat Detectors for Fire Protective Signaling Systems |
| No. 464 | Audible Signaling Appliances |
| No. 38 | Manually Actuated Signaling Boxes |
| No. 1481 | Power Supplies for Fire Protective Signaling Systems |
| No. 346 | Waterflow Indicators for Fire Protective Signaling Systems |
| No. 1076 | Control Units for Burglar Alarm Proprietary Protective Signaling Systems |
| No. 1971 | Visual Notification Appliances |
| No. 2017 | Standard for General-Purpose Signaling Devices and Systems |
| No.60950 | Safety of Information Technology Equipment |

D.	Local and State Building Codes.

E.	All requirements of the Authority Having Jurisdiction (AHJ).

1.6	APPROVALS:

A.	The system shall have proper listing and/or approval from the following nationally recognized agencies:

| UL | Underwriters Laboratories, Inc |
| --- | --- |
| ULC | Underwriters Laboratories Canada |
| FM | Factory Mutual |
| NYFD | New York Fire Department |
| CSFM | California State Fire Marshal |

The system shall be listed by the national agencies as suitable for extinguishing release applications. The system shall support release of low pressure CO2.

B.	The system shall be approved for use in Marine applications by the following agencies.

1.	United States Coast Guard

2.	Lloyd’s Register

3.	American Bureau of Shipping

C.	The system shall be certified for seismic applications in accordance with the International Building Code (IBC).  For OSHPD applications in California the system shall be Pre-Approved for seismic applications.  The basis for qualification of seismic approval shall be via shake table testing.

PART 2.0	PRODUCTS

2.1	Main Fire Alarm Control Panel or Network Node:

A.	Main FACP or network node shall be a NOTIFIERJohnson ControlsHoneywell Model NFS2-640IFC2-640XLS140-2 and shall contain a microprocessor based Central Processing Unit (CPU) and power supply in an economical space saving single board design. The CPU shall communicate with and control the following types of equipment used to make up the system: intelligent addressable smoke and thermal (heat) detectors, addressable modules, printer, annunciators, and other system controlled devices.

2.2	System Capacity and General Operation

A.	The FACP shall be capable of communicating on Noti-Fire-Net over a Local Area Network (LAN) or Wide Area Network (WAN) utilizing a peer-to-peer, inherently regenerative communication format and protocol.  The network shall support communication speed up to 100 Mb and support up to 200 panels / nodes per network.

B.	Each network node shall provide, or be capable of 318 intelligent / addressable devices per SLC loop.The Notification Appliance Circuits shall be programmable to Synchronize with System Sensor, Gentex and Wheelock Notification Appliances.

C.	The system shall include a full featured operator interface control and annunciation panel that shall include a backlit Liquid Crystal Display (LCD), individual color coded system status LEDs, and an alphanumeric keypad with easy touch rubber keys for the field programming and control of the fire and gas and gas detection system.

D.	The system shall be programmable, configurable, and expandable in the field without the need for special tools, PROM programmers or PC based programmers. It shall not require replacement of memory ICs to facilitate programming changes.

E.	The system shall allow the programming of any input to activate any output or group of outputs. Systems that have limited programming (such as general alarm), have complicated programming (such as a diode matrix), or require a laptop personal computer are not considered suitable substitutes.

F.	The FACP shall support up to 20 logic equations, including "and," "or," and "not," or time delay equations to be used for advanced programming. Logic equations shall require the use of a PC with a software utility designed for programming.

G.	The FACP or each network node shall provide the following features:

1.	Drift compensation to extend detector accuracy over life. Drift compensation shall also include a smoothing feature, allowing transient noise signals to be filtered out.

2.	Detector sensitivity test, meeting requirements of NFPA 72.

3.	Maintenance alert, with two levels (maintenance alert/maintenance urgent), to warn of excessive smoke detector dirt or dust accumulation.

4.	Up to nine sensitivity levels for alarm, selected by detector. The alarm level range shall be 0.5 to 2.35 percent per foot for photoelectric detectors, 0.5 to 2.5 percent per foot for ionization detectors,, 0.5 to 4.0 percent per foot for acclimate detectors and 1.0 to 4.0 percent per foot for multi-criteria (IntelliQuad and IntelliQuad PLUS) detectors  The system shall also support sensitive advanced detection laser detectors with an alarm level range of .02 percent per foot to 2.0 percent per foot. The system shall also include up to nine levels of Pre-alarm, selected by detector, to indicate impending alarms to maintenance personnel.

5.	The ability to display or print system reports.

6.	Alarm verification, with counters and a trouble indication to alert maintenance personnel when a detector enters verification 20 times.

7.	PAS presignal, meeting NFPA 72 requirements.

8.	Self optimizing pre-alarm for advanced fire warning, which allows each detector to learn its particular environment and set its prealarm level to just above normal peaks.

9.	Cross zoning with the capability of counting: two detectors in alarm, two software zones in alarm, or one smoke detector and one thermal detector.

10.	Control-by-time for non-fire operations, with holiday schedules.

11.	Day/night automatic adjustment of detector sensitivity.

12.	Device blink control for sleeping areas.

13.	The FACP shall be capable of coding main panel node notification circuits in March Time (120 PPM), Temporal (NFPA 72 A-2-2.2.2), and California Code. Panel notification circuits (NAC 1,2,3 and 4) shall also support Two-Stage operation, Canadian Dual Stage (3 minutes) and Canadian Dual Stage (5 minutes). Two stage operation shall allow 20 Pulses Per Minute (PPM) on alarm and 120 PPM after 5 minutes or when a second device activates. Canadian Dual stage is the same as Two-Stage except will only switch to second stage by activation of Drill Switch 3 or 5 minute timer. The panel shall also provide a coding option that will synchronize specific strobe lights designed to accept a specific "sync pulse."

14.	Network CommunicationThe FACP shall be capable of communicating with a Distributed Control System

15.	For flexibility and to ensure program validity, an optional Windows(TM) based program utility shall be available. This program shall be used to off-line program the system with batch upload/download, and have the ability to upgrade the manufacturers (FLASH) system code changes. This program shall also have a verification utility, which scans the program files, identifying possible errors. It shall also have the ability to compare old program files to new ones, identifying differences in the two files to allow complete testing of any system operating changes. This shall be in compliance with the NFPA 72 requirements for testing after system modification.

a.	This utility shall provide the ability to create and print NFPA style Test and Inspection reports

b.	This utility shall provide the ability to create and print Device Maintenence information

16.	The 80-character display keypad shall be an easy to use QWERTY type keypad, similar to a PC keyboard. This shall be part of the standard system and have the capability to command all system functions, entry of any alphabetic or numeric information, and field programming. Two different password levels shall be provided to prevent unauthorized system control or programming.

17.	When configured with an optional 640-character display the display shall use 10 "soft" keys for screen navigation or to accomplish dedicated programming functions.  Full programming access shall require use of a laptop and the proper programming utility.  With the 640 display option the system shall support distributed audio amplifiers on the digital audio loop of the Digital Voice Command.

H.	Signaling Line Circuits (SLC)

1.	Each FACP or FACP network node shall support up to two SLCs. Each SLC interface shall provide power to and communicate with up to 159 intelligent detectors (onization, photoelectric, multi-criteria, thermal, laser, fire/CO) and 159 intelligent modules (monitor, control, relay, releasing) for a loop capacity of 318 devices. The addition of the optional second loop shall double the device capacity, supporting a total of 636 devices.  Each SLC shall be capable of NFPA 72 Style 4, Style 6, or Style 7 (Class A or B) wiring.

2.	CPU shall receive analog information from all intelligent detectors to be processed to determine whether normal, alarm, prealarm, or trouble conditions exist for each detector. The software shall automatically maintain the detector's desired sensitivity level by adjusting for the effects of environmental factors, including the accumulation of dust in each detector. The analog information shall also be used for automatic detector testing and for the automatic determination of detector maintenance requirements.

- Serial Interfaces

1.	The system shall include two serial EIA-232 interfaces. Each interface shall be a means of connecting UL Listed Information Technology Equipment (ITE) peripherals.

a.	EIA-232 interface shall be used to connect an UL-Listed 40 or 80 column printer. Printers that are not UL-Listed are not considered acceptable substitutes.

b.	The system shall include an EIA-485 port for the serial connection of optional annunciators and remote LCD displays.

c.	The EIA-485 interface may be used for network connection to a proprietary-receiving unit.

J.	Digital Voice Command Center

1.	The Digital Voice Command Center located with the FACP, shall contain all equipment required for all audio control, emergency telephone system control, signaling and supervisory functions. This shall include speaker zone indication and control, telephone circuit indication and control, digital voice units, microphone and main telephone handset.  The DVC shall support up to 8 channels of voice when configured with Digital Audio Amplifiers and 4 channels of voice when employing the optional analog output card.  Each DVC shall support up to 32 digital audio amplifiers.

2.	Function: The Voice Command Center equipment shall perform the following functions:

a.	Operate as a supervised multi-channel emergency voice communication system.

b.	Operate as a two-way emergency telephone system control center.

Audibly and visually annunciate the active or trouble condition of every speaker circuit and emergency telephone circuit.

c.	Audibly and visually annunciate any trouble condition for digital tone and voice units required for normal operation of the system.

d.	Provide all-call Emergency Paging activities through activation of a single control switch.

e.	As required, provide vectored paging control to specific audio zones via dedicated control switches.

f.	Provide a factory recorded "library" of voice messages and tones in standard WAV. File format, which may be edited and saved on a PC running a current Windows® operating system.

g.	Provide a software utility capable of off-line programming for the DVCoperation and the audio message files.  This utility shall support the creation of new programs as well as editing and saving existing program files.   Uploading or downloading the DVC  shall not inhibit the emergency operation of other nodes on the fire alarm network.

h.	Support an optional mode of operation with four analog audio outputs capable of being used with UL 864 fire-listed analog audio amplifiers and SLC  controlled switching.

i.	The Digital Voice Command shall be modular in construction, and shall be capable of being field programmable without requiring the return of any components to the manufacturer and without requiring use of any external computers or other programming equipment.

j.	The Digital Voice Command and associated equipment shall be protected against unusually high voltage surges or line transients.

3.	The emergency voice alarm communication system shall incorporate a Two-way emergency telephone communication system.

a.	Two-way emergency telephone communication circuits shall be supervised for open and short circuit conditions.

b.	Two-way emergency telephone (Fire Fighter Telephone) communication shall be supported between the Digital Voice Audio Command Center and up to seven (7) remote Fire Fighter's Telephone locations simultaneously on a telephone riser.

c.	Means shall be provided to connect FFT voice communications to the speaker circuits in order to allow voice paging over the speaker circuit from a telephone handset.

K.	Audio Amplifiers

1.	The Audio Amplifiers will provide Audio Power (@25 Volt RMS or 70 RMS ) for distribution to speaker circuits.

2.	Multiple audio amplifiers may be mounted in a single enclosure, either to supply incremental audio power, or to function as an automatically switched backup amplifier(s).

3.	The audio amplifier shall include an integral power supply, and shall provide built-in LED indicators for the following conditions:

a.	Earth Fault on DAP A (Digital Audio Port A)

b.	Earth Fault on DAP B (Digital Audio Port B)

c.	Audio Amplifier Failure Detected Trouble

d.	Active Alarm Bus input

e.	Audio Detected on Aux Input A

f.	Audio Detected on Aux Input B

g.	Audio Detected on Firefighter's Telephone Riser

h.	Receiving Audio from digital audio riser

i.	Short circuit on speaker circuit 1

j.	Short circuit on speaker circuit 2

k.	Short circuit on speaker circuit 3

l.	Short circuit on speaker circuit 4

m.	Data Transmitted on DAP A

n.	Data Received on DAP A

o.	Data Transmitted on DAP B

p.	Data Received on DAP B

q.	Board failure

r.	Active fiber optic media connection on port A (fiber optic media applications)

s.	Active fiber optic media connection on port B (fiber optic media applications)

t.	Power supply Earth Fault

u.	Power supply 5V present

v.	Power supply conditions - Brownout, High Battery, Low Battery, Charger Trouble

4.	The audio amplifier shall provide the following built-in controls:

a.	Amplifier Address Selection Switches

b.	Signal Silence of communication loss annunciation Reset

c.	Level adjustment for background music

d.	Enable/Disable for Earth Fault detection on DAP A

e.	Enable/Disable for Earth Fault detection on DAP A

f.	Switch for 2-wire/4-wire FFT riser

5.	Adjustment of the correct audio level for the amplifier shall not require any special tools or test equipment.

6. 	Includes audio input and amplified output supervision, back up input, and automatic switch over function, (if primary amplifier should fail).

7. 	System shall be capable of backing up digital amplifiers.

8. 	One-to-one backup shall be provided by either a plug-in amplifier card or a designated backup amplifier of identical model as the primary amplifier.

9. 	One designated backup amplifier shall be capable of backing up multiple primary amplifiers mounted in the same or adjacent cabinets.

10. 	Multi-channel operation from a single amplifier shall be supported by the addition of an optional plug-in amplifier card.

L.	Audio Message Generator (Prerecorded Voice)/Speaker Control:

1.	Each initiating zone or intelligent device shall interface with an emergency voice communication system capable of transmitting a prerecorded voice message to all speakers in the building.

2.	Actuation of any alarm initiating device shall cause a prerecorded message to sound over the speakers. The message shall be repeated four (4) times.  Pre- and post-message tones shall be supported.

3.	A built-in microphone shall be provided to allow paging through speaker circuits.

4.	System paging from emergency telephone circuits shall be supported.

5.	The audio message generator shall have the following indicators and controls to allow for proper operator understanding and control:

a.	Lamp Test

b.	Trouble

c.	Off-Line Trouble

d.	Microphone Trouble

e.	Phone Trouble

f.	Busy/Wait

g.	Page Inhibited

h.	Pre/Post Announcement Tone

M.	Controls with associated LED Indicators:

1.	Speaker Switches/Indicators

a.	The speaker circuit control switches/indicators shall include visual indication of active and trouble status for each speaker circuit in the system.

b. 	The speaker circuit control panel shall include switches to manually activate or deactivate each speaker circuit in the system.

2.	Emergency Two-Way Telephone Control Switches/Indicators

a.	The emergency telephone circuit control panel shall include visual indication of active and trouble status for each telephone circuit in the system.

b. 	The telephone circuit control panel shall include switches to manually activate or deactivate each telephone circuit in the system.

N.	Specific System Operations

1.	Smoke Detector Sensitivity Adjust: A means shall be provided for adjusting the sensitivity of any or all addressable intelligent detectors in the system from the system keypad. Sensitivity range shall be within the allowed UL window and have a minimum of 9 levels.

2.	Alarm Verification: Each of the intelligent addressable smoke detectors in the system may be independently selected and enabled to be an alarm verified detector. The alarm verification delay shall be programmable from 0 to 60 seconds and each detector shall be able to be selected for verification. The FACP shall keep a count of the number of times that each detector has entered the verification cycle. These counters may be displayed and reset by the proper operator commands.

3.	Point Disable: Any addressable device  in the system may be enabled or disabled through the system keypad.

4.	Point Read: The system shall be able to display or print the following point status diagnostic functions:

a.	Device status

b.	Device type

c.	Custom device label

d.	View analog detector values

e.	Device zone assignments

5.	System History Recording and Reporting: The fire alarm control panel shall contain a history buffer that will be capable of storing up to 800 events. Up to 200 events shall be dedicated to alarm and the remaining events are general purpose. Systems that do not have dedicated alarm storage, where events are overridden by non-alarm type events, are not suitable substitutes. Each of these activations will be stored and time and date stamped with the actual time of the activation. The contents of the history buffer may be manually reviewed, one event at a time, or printed in its entirety. The history buffer shall use non-volatile memory. Systems that use volatile memory for history storage are not acceptable substitutes.

6.	Automatic Detector Maintenance Alert: The fire alarm control panel shall automatically interrogate each intelligent detector and shall analyze the detector responses over a period of time. If any intelligent detector in the system responds with a reading that is above or below normal limits, then the system will enter the trouble mode, and the particular detector will be annunciated on the system display, and printed on the optional printer. This feature shall in no way inhibit the receipt of alarm conditions in the system, nor shall it require any special hardware, special tools or computer expertise to perform.

7.	Pre-Alarm Function: The system shall provide two levels of pre-alarm warning to give advance notice of a possible fire situation. Both pre-alarm levels shall be fully field adjustable. The first level shall give an audible indication at the panel. The second level shall give an audible indication and may also activate control relays. The system shall also have the ability to activate local detector sounder bases at the pre-alarm level, to assist in avoiding nuisance alarms.

8.	Software Zones: The FACP shall support 142 independent programmable software zones

9.	The fire alarm control panel shall include a walk test feature. It shall include the ability to test initiating device circuits and notification appliance circuits from the field without returning to the panel to reset the system. Operation shall be as follows:

a.	Alarming an initiating device shall activate programmed outputs, which are selected to participate in walk test, for 3 seconds.

b.	Introducing a trouble into the initiating device shall activate the programmed outputs for 8 seconds.

c.	All devices tested in walk test shall be recorded in the history buffer.

10.	Multiple agent releasing zones: The system shall support up to 10 releasing zones to protect against 10 independent hazards. Releasing zones shall provide up to three cross-zone and four abort options to satisfy any local jurisdiction requirements.

11.	Mass Notification Override:The system shall be UL 2572 listed for Mass Notification and shall be capable, based on the Risk Analysis, of being programmed so that Mass Notification/Emergency Communications events take precedence over fire alarm events.

O.	Conventional Aspirating Detection

1.	An optional air aspiration detection system shall be available.

2.	The aspirating system shall support multiple sensitivity settings.

3.	The aspirating system shall operate from 24 VDC.

4.	The aspirating system shall provide alarm and trouble relays used to activate a fire alarm control panel.

P.	Aspiration System Interface:

1.	The system shall be capable of supporting Interface Modules for integrating Vesda Aspiration detectors into SLC loop of the fire alarm control panel. The Interface Module shall support up to 19 detectors detectors, each SLC loop shall support one interface module.

Q.	High Level Aspiration System Interface:

1.	The system shall be capable of supporting a High Level Interface for Vesda Aspirating Detection Systems.  The interface shall support up to 100 detectors and allow the fire alarm network to monitor and control events on the aspiration system.

R.	Portable Emergency Telephone Handset Jack

1.	Portable emergency telephone handset jacks shall be flush mounted on stainless steel plates as indicated on the plans. Jacks shall be approved for emergency telephone system application.

2.	Insertion of a portable handset plug into a jack shall send a signal to the fire command center, which shall audibly and visually indicate the on-line condition, and shall sound a "ring" indication in the handset.

3.	The two-way emergency telephone system shall support a minimum of seven (7) handsets on line without degradation of the signal.

S.	Fixed Emergency Telephone Handset

1.	The telephone cabinet shall be painted red and clearly labeled as "Emergency Telephone." The cabinets shall be located where shown on drawings.

2.	The handset cradle shall have a switch connection so that lifting the handset off of the cradle shall send a signal to the fire command center, which shall audibly and visually indicate its on-line (off-hook) condition.

3.	On activating the remote phone, the phone earpiece shall sound a telephone ring signal until the master handset is lifted.

4.	The two-way emergency telephone system shall support a minimum of seven (7) handsets on line without degradation of the signal.

T.	All interfaces and associated equipment are to be protected so that they will not be affected by voltage surges or line transients consistent with UL standard 864.

U.	Communicators

1.	The UDACT shall be compact in size, mounting in a standard module position of the fire alarm control cabinet. Optionally, the UDACT shall have the ability for remote mounting, up to 6,000 feet from the fire alarm control panel. The wire connections between the UDACT and the control panel shall be supervised with one pair for power and one pair for multiplexed communication of overall system status.  Systems that utilize relay contact closures are not acceptable.

2.	The UDACT shall include connections for dual telephone lines (with voltage detect), per UL/NFPA/FCC requirements. It shall include the ability for split reporting of panel events up to two different telephone numbers.

The UDACT shall be capable of transmitting events in 4+2, SIA, and Contact ID.

Communication shall include vital system status such as:

a.	Independent Zone (Alarm, trouble, non-alarm, supervisory)

b.	Independent Addressable Device Status

c.	AC (Mains) Power Loss

d.	Low Battery and Earth Fault

e.	System Off Normal

f.	12 and 24 Hour Test Signal

g.	Abnormal Test Signal (per UL requirements)

h.	EIA-485 Communications Failure

i.	Phone Line Failure

3.	The UDACT shall support independent zone/point reporting when used in the Contact ID format. In this format the UDACT shall support transmission of up to 3,064 points. This enables the central station to have exact details concerning the origin of the fire or response emergency.

4.	The UDACT shall be capable of being programmed with the same programming utility as the host FACP, and saved, edited and uploaded and downloaded using the utility.  UDACT shall be capable of being programmed online or offline.  The programming utility shall also support upgrading UDACT operating firmware.

5.	The UDACT shall be capable of generating Central Station reports providing detailed programming information for each point along with the central station point address.

6.	An IP or IP/GSM Communicator option shall be available to interface to the UDACT and be capable of transmitting signals over the internet/intranet or Cellular (GSM) network to a compatible receiver.

V.	Smoke Control Annunciator

1.	On/Auto/Off switches and status indicators (LEDS) shall be provided for monitoring and manual control of each fan, damper, HVAC control unit, stairwell pressurization fan, and smoke exhaust fan. To ensure compliance the units supplied shall meet the following UL categories: UUKL, PAZX, UDTZ, QVAX as well as the requirements of NFPA 90A, HVAC, and NFPA 92A & 92B, Smoke Control. The control System shall be field programmable for either 90A operation or 92A/B operation to allow for future use and system expansion.

2.	The OFF LED shall be Yellow, the ON LED shall be green, the Trouble/Fault LED shall be Amber/Orange for each switch. The Trouble/Fault indicator shall indicate a trouble in the control and/or monitor points associated with that switch. In addition, each group of eight switches shall have two LEDS and one momentary switch which allow the following functions: An Amber LED to indicate an OFF-NORMAL switch position, in the ON or OFF position; A Green LED to indicate ALL AUTO switch position; A Local Acknowledge/Lamp Test momentary switch.

3.	Each switch shall have the capability to monitor and control two addressable inputs and two addressable outputs. In all modes, the ON and OFF indicators shall continuously follow the device status not the switch position. Positive feedback shall be employed to verify correct operation of the device being controlled. Systems that indicate on/off/auto by physical switch position only are not acceptable.

4.	All HVAC switches (i.e., limit switches, vane switches, etc.) shall be provided and installed by the HVAC contractor.

5.	It shall be possible to meet the requirements mentioned above utilizing wall mounted custom graphic.

2.3	Gateway & Webserver Options

A.	Common Alerting Protocol (CAP) Gateway: The system shall support an optional CAP Gateway (Common Alerting Protocol).  The CAP Gateway translates fire system messages to industry standard CAP messages for integration with CAP-compliant clients. A CAP gateway shall be available from the fire alarm control panel manufacturer.

B.	LEDSIGN Gateway: The system shall support an optional and proprietary LEDSIGN Gateway to interface to LED signs that will automatically display emergency messages.  The signs shall be capable of storing up to 100 messages that can be activated via system programming with the ability to be manually overridden.  The Sign Gateway shall support up to 10 independent signs, each sign capable of playing an independent message.  Multiple LEDSIGN Gateways can be used in network applications. An LEDSIGN gateway shall be available from the fire alarm control panel manufacturer.

C.	BACnet Interface Gateway: The system shall be capable of being interfaced with BACNet compliant clients. A BACnet interface supporting BACnet/IP communication shall be available from the fire alarm control panel manufacturer.

D.	MODbus Interface Gateway: The system shall be capable of being interfaced with MODbus compliant clients. A MODbus interface supporting MODbus/TCP communication shall be available from the fire alarm control panel manufacturer.

E.	Noti-Fire-Net Gateway: The system shall support an IP based gateway to enable the panel or local Noti-Fire-Net to be connected to an ONYXWorks workstation via the Internet or Intranet. This gateway shall also support the ability to integrate the system to an interactive firefighter’s display. The Noti-Fire-Net Gateway shall be available from  the fire alarm control manufacturer.

F.	Webserver:  The system shall support a webserver allowing remote connection via the Internet or Intranet. Authorized users will have the ability to view panel/network history, event status and device properties.  The webserver shall also support sending event information via email or text to up to 50 registered users, the webserver shall be available from the fire alarm control panel manufacturer.

G.	Web Portal Interface:  The system shall be capable of being interfaced with a web portal to integrate with Inspection and Service Manager utilities.  The web portal and inspection and service manager utilities shall be available from the fire alarm control panel manufacturer.

2.4	System Components - Addressable Devices

A.	Addressable Devices - General

1.	Addressable devices shall use simple to install and maintain decade, decimal address switches. Devices shall be capable of being set to an address in a range of 001 to 159.

2.	Addressable devices, which use a binary-coded address setting method, such as a DIP-switch, are not an allowable substitute. Addressable devices that require the address be programmed using a special tool or programming utility are not an allowable substitute.

3.	Detectors shall be intelligent (analog) and addressable, and shall connect with two wires to the fire alarm control panel Signaling Line Circuits.

4.	Addressable smoke and thermal detectors shall provide dual alarm and power/polling LEDs. Both LEDs shall flash green under normal conditions, indicating that the detector is operational and in regular communication with the control panel, and both LEDs shall be placed into steady red illumination by the control panel, indicating that an alarm condition has been detected. If required, the LED flash shall have the ability to be removed from the system program. An output connection shall also be provided in the base to connect an external remote alarm LED.

5.	The fire alarm control panel shall permit detector sensitivity adjustment through field programming of the system. The panel on a time-of-day basis shall automatically adjust sensitivity.

6.	Using software in the FACP, detectors shall automatically compensate for dust accumulation and other slow environmental changes that may affect their performance. The detectors shall be listed by UL as meeting the calibrated sensitivity test requirements of NFPA Standard 72.

7.	The detectors shall be ceiling-mount and shall include a separate twist-lock base with tamper proof feature. Base options shall include a sounder base with a built-in (local) sounder rated at 85 DBA minimum, a relay base and an isolator base designed for Style 7 applications. The system shall also support an intelligent programmable sounder base, the programmable sounder base shall be capable of providing multiple tones based on programming and at a minimum be capable of providing a Temp-4 tone for CO (Carbon Monoxide) activation and a Temp-3 tone for fire activations and be capable of being synchronized with other programmable sounder bases and common area notification appliances; 85 DBA minimum.

8.	The detectors shall provide a test means whereby they will simulate an alarm condition and report that condition to the control panel. Such a test may be initiated at the detector itself (by activating a magnetic switch) or initiated remotely on command from the control panel.

9.	Detectors shall also store an internal identifying type code that the control panel shall use to identify the type of device (ION, PHOTO, THERMAL).

10.	Detectors will operate in an analog fashion, where the detector simply measures its designed environment variable and transmits an analog value to the FACP based on real-time measured values. The FACP software, not the detector, shall make the alarm/normal decision, thereby allowing the sensitivity of each detector to be set in the FACP program and allowing the system operator to view the current analog value of each detector.

11.	Addressable devices shall store an internal identifying code that the control panel shall use to identify the type of device.

12.	A magnetic test switch shall be provided to test detectors and modules. Detectors shall report an indication of an analog value reaching 100% of the alarm threshold.

13.	Addressable modules shall mount in a 4-inch square (101.6 mm square), 2-1/8 inch (54 mm) deep electrical box. An optional surface mount Lexan enclosure shall be available.

B.	Addressable Manual Fire Alarm Box (manual station)

1.	Addressable manual fire alarm boxes shall, on command from the control panel, send data to the panel representing the state of the manual switch and the addressable communication module status;NOTIFIER model # NBG-12LX.  They shall use a key operated test-reset lock, and shall be designed so that after actual emergency operation, they cannot be restored to normal use except by the use of a key.

2.	All operated stations shall have a positive, visual indication of operation and utilize a key type reset.

3.	Manual fire alarm boxes shall be constructed of Lexan with clearly visible operating instructions provided on the cover. The word FIRE shall appear on the front of the stations in raised letters, 1.75 inches (44 mm) or larger.

C.	Intelligent Photoelectric Smoke Detector: The intelligent photoelectric smoke detector shall be NOTIFIER model # FSP-851 and shall use the photoelectric (light-scattering) principal to measure smoke density and shall, on command from the control panel, send data to the panel representing the analog level of smoke density.

D.	Intelligent VIEW® Laser Photo Smoke Detector: The intelligent laser photo smoke detector shall be a spot type detector, NOTIFIER model # FSL-751, that incorporates an extremely bright laser diode and an integral lens that focuses the light beam to a very small volume near a receiving photo sensor. The scattering of smoke particles shall activate the photo sensor.

1.	The laser detector shall have conductive plastic so that dust accumulation is reduced significantly.

2.	The intelligent laser photo detector shall have nine sensitivity levels and be sensitive to a minimum obscuration of 0.02 percent per foot.

3.	The laser detector shall not require expensive conduit, special fittings or PVC pipe.

4.	The intelligent laser photo detector shall support standard, relay, isolator and sounder detector bases.

5.	The laser photo detector shall not require other cleaning requirements than those listed in NFPA 72. Replacement, refurbishment or specialized cleaning of the detector head shall not be required.

6.	The laser photo detector shall include two bicolor LEDs that flash green in normal operation and turn on steady red in alarm.

E.	Intelligent Ionization Smoke Detector: The intelligent ionization smoke detector shall be NOTIFIER model # FSI-851 and shall use the dual-chamber ionization principal to measure products of combustion and shall, on command from the control panel, send data to the panel representing the analog level of products of combustion.

F.	Intelligent Multi Criteria Acclimating Detector: The intelligent multi-criteria Acclimate® Plus™ detector shall be an addressable device, NOTIFIER model # FAPT-851, that is designed to monitor a minimum of photoelectric and thermal technologies in a single sensing device. The design shall include the ability to adapt to its environment by utilizing a built-in microprocessor to determine its environment and choose the appropriate sensing settings. The detector design shall allow a wide sensitivity window, no less than 1 to 4% per foot obscuration. This detector shall utilize advanced electronics that react to slow smoldering fires and thermal properties all within a single sensing device.

1.	The microprocessor design shall be capable of selecting the appropriate sensitivity levels based on the environment type it is in (office, manufacturing, kitchen etc.) and then have the ability to automatically change the setting as the environment changes (as walls are moved or as the occupancy changes).

2.	The intelligent multi criteria detection device shall include the ability to combine the signal of the thermal sensor with the signal of the photoelectric signal in an effort to react hastily in the event of a fire situation. It shall also include the inherent ability to distinguish between a fire condition and a false alarm condition by examining the characteristics of the thermal and smoke sensing chambers and comparing them to a database of actual fire and deceptive phenomena.

G.	Intelligent Thermal Detectors: The intelligent thermal detectors shall be NOTIFIER FST- series addressable devices rated at 135 degrees Fahrenheit (58 degrees Celsius) and have a rate-of-rise element rated at 15 degrees F (9.4 degrees C) per minute.  A high heat thermal detector rated at 190 degrees Fahrenheit shall also be available.  The thermal detectors shall connect via two wires to the fire alarm control panel signaling line circuit.

H.	Intelligent Duct Smoke Detector: The smoke detector housing shall accommodate an intelligent photoelectric detector that provides continuous analog monitoring and alarm verification from the panel.  When sufficient smoke is sensed, an alarm signal is initiated at the FACP, and appropriate action taken to change over air handling systems to help prevent the rapid distribution of toxic smoke and fire gases throughout the areas served by the duct system.  The Intelligent Duct Smoke Detector shall support the installation of addressable Photoelectric detector capable or being tested remotely.  The Intelligent Duct Detector housing shall be model # DNR(W) and the remote test capable photoelectric smoke detector shall be NOTIFIER model # FSP-851R.

I.	IntelliQuad™ Advanced Multi-Criteria Intelligent Detector

1.	Intelligent multi-criteria fire detector shall be a NOTIFIER model number FSC-851.  Smoke detector shall be an addressable intelligent multi-criteria smoke detector. The detector shall be comprised of four sensing elements, including a photoelectric (light-scattering) particulate sensor, an electrochemical carbon monoxide (CO) sensor, a daylight-filtered infrared sensor and solid state thermal sensor(s) rated at 135°F (57.2°C).   The device shall be able to indicate distinct smoke and heat alarms.

2.	The intelligent multi-criteria detection device shall include the ability to combine the signal of the photoelectric signal with other sensing elements in an effort to react quickly in the event of a fire situation.  It shall also include the inherent ability to distinguish between a fire condition and a nuisance alarm condition.  The product design shall be capable of selecting the appropriate sensitivity levels based on the environment type chosen by user in which it is installed (office, manufacturing, kitchen etc.) and then have the ability to automatically change the setting as the environment changes.

3.	The detector shall be capable of automatically adjusting its sensitivity by means of drift compensation and smoothing algorithms.  The detector shall be capable of automatically adjusting its sensitivity by means of drift compensation and smoothing algorithms.  The device shall provide unique signals to indicate when 20% of the drift range is remaining, when 100% of drift range is used, and when there is a chamber fault to show unit requires maintenance.

4.	The detector shall indicate CO trouble conditions including 6 months of sensor life remaining and sensor life has expired.  The detector shall indicate a combined signal for any of the following:  low chamber trouble, thermistor trouble, CO self test failure, IR self test failure, and freeze warning.

5.	The detectors shall provide address-setting means on the detector head using rotary switches.  Because of the possibility of installation error, systems that use binary jumpers or DIP switches to set the detector address are not acceptable.  The detectors shall also store an internal identifying code that the control panel shall use to identify the type of detector.  Systems that require a special programmer to set the detector address (including temporary connection at the panel) are labor intensive and not acceptable. Each detector occupies any one of at least 99 possible addresses on the signaling line circuit (SLC) loop.  It responds to regular polls from the system and reports its type and status.

6.	The detectors shall provide a test means whereby they will simulate an alarm condition and report that condition to the control panel. Such a test may be initiated at the detector itself (by activating a switch) or initiated remotely on command from the control panel.  There are three test methods:  functional magnet, smoke entry aerosol, or direct heat method.

7.	The detectors shall provide two LEDs to provide 360° visibility.  The LEDs are placed into steady red illumination by the control panel indicating that an alarm condition has been detected.  An output connection shall also be provided in the base to connect an external remote alarm LED, sounder base, and / or relay base (optional accessories).  The external remote alarm can be interconnected to other sounder or relay bases for activating all devices in a space via a single alarming unit.

8.	Two LEDs on the sensor are controlled by the panel to indicate sensor status. Coded signals, transmitted from the panel, can cause the LEDs to blink, latch on, or latch off. Refer to the control panel technical documentation for sensor LED status operation and expected delay to alarm.

9.	The detectors shall be ceiling-mount and shall be plug-in mounted into a twist-lock base.   These detectors shall be constructed of off-white UV resistant polymer and shall be detachable from the mounting base to simplify installation, service and maintenance. Mounting base wiring connections shall be made by means of SEMS screws. The detector shall allow pre-wiring of the base and the head shall be a plug-in type.   Mounting base shall be mounted on junction box which is at least 1.5 inches (3.81 cm) deep. Mounting base shall be available to mount to standard junction boxes.  Suitable boxes include:

a.	4.0" (10.16 cm) square box with and without plaster ring.

b.	4.0" (10.16 cm) octagonal box.

c.	3.5" (8.89 cm) octagonal box.

d.	Single-gang box.

10.	Meets Agency Standards

a.	ANSI/UL 268 -Smoke Detectors for Fire Alarm Signaling Systems

b.	CAN/ULC-S529- Smoke Detectors for Fire Alarm Systems

c.	FM 3230-3250- Smoke Actuated Detectors for Automatic Fire Alarm Signaling

J.	IntelliQuad™ PLUS Advanced Multi-Criteria Intelligent Fire/CO Detector

1.	Advanced Multi-Criteria Fire/CO detector shall be NOTIFIER model # FCO-851 and shall be an addressable advanced multi-criteria smoke detector with a separate signal for carbon monoxide (CO) detection per UL 2075 standards.

2.	The detector shall be comprised of four sensing elements, including a photoelectric (light-scattering) particulate sensor, an electrochemical CO sensor, a daylight-filtered infrared (IR) sensor and solid state thermal sensor(s) rated at 135°F (57.2°C). The device shall be able to indicate distinct smoke and heat alarms.

3.	The advanced multi-criteria detection device shall include the ability to combine the signal of the photoelectric signal with other sensing elements in order to react quickly in the event of a fire situation. It shall also include the inherent ability to distinguish between a fire condition and a nuisance alarm condition. The detector shall be capable of selecting the appropriate sensitivity levels based on the environment type (office, manufacturing, kitchen, etc.) in which it is installed, and then have the ability to automatically change the setting as the environment changes.

4.	The CO detector component shall be capable of a functional gas test using a canned test agent to test the functionality of the CO sensing cell.

5.	The detector shall be capable of automatically adjusting its sensitivity by means of drift compensation and smoothing algorithms. The device shall provide unique signals to indicate when 20 percent of the drift range is remaining, when 100 percent of drift range is used, and when there is a chamber fault to show the unit requires maintenance.

6.	The detector shall indicate CO trouble conditions, including six months of sensor life remaining and sensor life has expired. The detector shall indicate a combined signal for any of the following: low chamber trouble, thermistor trouble, CO self test failure, IR self test failure, and freeze warning.

7.	The detector shall provide address-setting means on the detector head using rotary switches. Because of the possibility of installation error, systems that use binary jumpers or DIP switches to set the detector address are not acceptable. The detector shall also store an internal identifying code that the control panel shall use to identify the type of detector. Systems that require a special programmer to set the detector address (including temporary connection at the panel) are labor intensive and not acceptable. Each detector occupies any one of at least 159 possible addresses on the signaling line circuit (SLC) loop. It responds to regular polls from the system and reports its type and status.

8.	The detector shall provide a test means whereby it will simulate an alarm condition and report that condition to the control panel. Such a test may be initiated at the detector itself (by activating a switch) or initiated remotely on command from the control panel. There shall be four test methods: functional magnet, smoke entry aerosol, carbon monoxide aerosol or direct heat method.

9.	The detector shall provide two LEDs to provide 360° visibility. The LEDs shall be placed into steady red illumination by the control panel indicating that an alarm condition has been detected. An output connection shall also be provided in the base to connect an external remote alarm LED. The detector must be capable of connecting to a sounder base that provides both temporal 3 and temporal 4 patterns for fire and CO alarm.

10.	Two LEDs on the sensor shall be controlled by the panel to indicate sensor status. Coded signals, transmitted from the panel, shall cause the LEDs to blink, latch on, or latch off. Refer to the control panel technical documentation for sensor LED status operation and expected delay to alarm.

11.	The detector shall be plug-in mounted into a twist-lock base. The detector shall be constructed of off-white, UV-resistant polymer and shall be detachable from the mounting base to simplify installation, service and maintenance. Mounting base wiring connections shall be made by means of SEMS screws. The detector shall allow pre-wiring of the base and the head shall be a plug-in type. The mounting base shall be mounted on a junction box that is at least 1.5 inches (3.81 cm) deep. The mounting base shall be available to mount to standard junction boxes.  Suitable boxes include:

a.	4.0" (10.16 cm) square box with and without plaster ring.

b.	4.0" (10.16 cm) octagonal box.

c.	3.5" (8.89 cm) octagonal box.

d.	Single-gang box.

e.	Double-gang box

12.	Meets Agency Standards

a.	ANSI/UL 268 -Smoke Detectors for Fire Alarm Signaling Systems

b.	CAN/ULC-S529- Smoke Detectors for Fire Alarm Systems

c.	FM 3230-3250- Smoke Actuated Detectors for Automatic Fire Alarm Signaling

d.	UL 2075 – Gas and Vapor Detector and Sensors – Systems Connected

K.	Intelligent Addressable Aspiration Detector: The intelligent aspiration detector shall be NOTIFIER model # FSA-8000 an addressable aspiration detector that communicates directly with the fire alarm control panel via the SLC communication protocol, no modules or high level interfaces shall be required. The fire alarm control panel shall support up to thirty one intelligent aspiration detectors per SLC loop. The aspiration detector shall have dual source (blue LED and infra-red laser) optical smoke detection for a wide range of fire detection with enhanced immunity to nuisance particulates. The FACP shall be capable of monitoring and annunciating up to five smoke event thresholds and eleven trouble conditions.  Each event threshold shall be capable of being assigned a discrete type ID at the FACP

L.	Intelligent Addressable Reflected Beam Detector

1.	The intelligent single-ended reflected beam smoke detector shall connect with two wires to the fire alarm control panel signaling line circuit (SLC).  The detectors shall consist of a transmitter/receiver unit and a reflector and shall send data to the panel representing the analog level of smoke density. The detector shall be capable of being tested remotely via a keyswitch; NOTIFIER model # FSB-200.  Model # FSB-200S shall be equipped with an integral sensitivity test feature

M.	Addressable Dry Contact Monitor Module

1.	Addressable monitor modules shall be provided to connect one supervised IDC zone of conventional alarm initiating devices (any N.O. dry contact device) to one of the fire alarm control panel SLCs.  The addressable monitor module shall be NOTIFIER model # FMM-1 (Class A or B) or FMM-101 (Class B)

2.	The IDC zone shall be suitable for Style D/Class A or Style B/Class B operation. An LED shall be provided that shall flash under normal conditions, indicating that the monitor module is operational and in regular communication with the control panel.

3.	For difficult to reach areas, the monitor module shall be available in a miniature package and shall be no larger than 2-3/4 inch (70 mm) x 1-1/4 inch (31.7 mm) x 1/2 inch (12.7 mm). This version need not include Style D or an LED.

4.	For multiple dry contact monitoring a module shall be available that provides 10 Style B or 5 Style D input circuits; NOTIFIER model # XP10-M.

N.	Two Wire Detector Monitor Module

1.	Addressable monitor modules shall be provided to connect one supervised IDC zone of conventional 2-wire smoke detectors or alarm initiating devices (any N.O. dry contact device); NOTIFIER model # FZM-1.

2.	The IDC zone may be wired for Class A or B (Style D or Style B) operation. An LED shall be provided that shall flash under normal conditions, indicating that the monitor module is operational and in regular communication with the control panel.

3.	For multiple 2-wire smoke detector circuit monitoring a module shall be available that provides 6 Style B/Class A or 3 Style D/Class B input circuits; NOTIFIER model # XP6-MA

O.	Addressable Control Module

1.	Addressable control modules shall be provided to supervise and control the operation of one conventional circuit of compatible Notification Appliances, 24 VDC powered, polarized audio/visual notification appliances; NOTIFIER model # FCM-1

2.	The control module NAC may be wired for Style Z or Style Y (Class A/B) with a current rating of 2 Amps for Style Z and 3 Amps for Style Y;

3.	Audio/visual power shall be provided by a separate supervised circuit from the main fire alarm control panel or from a supervised UL listed remote supply.

4.	For multiple circuit control a module shall be available that provides 6 Style Y (Class B) or 3 Style Z (Class A) control circuits; NOTIFIER model # XP6-C.

P.	Addressable Releasing Control Module

1.	An addressable FlashScan releasing module shall be available to supervise and control compatible releasing agent solenoids; NOTIFIER model # FCM-1-REL.

2.	The module shall operate on a redundant protocol for added protection.

3.	The module shall be configurable for Style Z or Style Y (Class  A/B) and support one 24 volt or two 12 volt solenoids.

Q.	Addressable Relay Module:

1.	Addressable Relay Modules shall be available for HVAC control and other network building functions; NOTIFIER model # FRM-1.

2.	The module shall provide two form C relays rated at up to 3 Amps resistive and up to 2.0 Amps inductive.

3.	The relay coil shall be magnetically latched to reduce wiring connection requirements, and to insure that 100% of all auxiliary devices energize at the same time on the same pair of wires.

4.	For multiple relay control a module shall be available that provides 6 programmable Form-C relays; NOTIFIER model # XP6-R.

R.	Addressable Two-In / Two-Out Monitor/Relay Module:

1.	An addressable Two-In / Two-Out module shall be available; NOTIFIER model # FDRM-1.

2.	The two-in/two-out module shall provide two Class B/Style B dry-contact input circuits and two independent Form-C relays rated at up to 3 Amps resistive and up to 2.0 Amps inductive.

S.	Isolator Module: Isolator modules shall be provided to automatically isolate wire-to-wire short circuits on an SLC Class A or Class B branch. The isolator module shall limit the number of modules or detectors that may be rendered inoperative by a short circuit fault on the SLC loop segment or branch. At least one isolator module shall be provided for each floor or protected zone of the building; NOTIFIER model # ISO-X.

1.	If a wire-to-wire short occurs, the isolator module shall automatically open-circuit (disconnect) the SLC. When the short circuit condition is corrected, the isolator module shall automatically reconnect the isolated section.

2.	The isolator module shall not require address-setting, and its operations shall be totally automatic. It shall not be necessary to replace or reset an isolator module after its normal operation.

3.	The isolator module shall provide a single LED that shall flash to indicate that the isolator is operational and shall illuminate steadily to indicate that a short circuit condition has been detected and isolated.

T.	Smoke Control Annunciator

1.	On/Auto/Off switches and status indicators (LEDS) shall be provided for monitoring and manual control of each fan, damper, HVAC control unit, stairwell pressurization fan, and smoke exhaust fan. To ensure compliance the units supplied shall meet the following UL categories: UUKL, PAZX, UDTZ, QVAX as well as the requirements of NFPA 90A, HVAC, and NFPA 92A & 92B, Smoke Control. The control System shall be field programmable for either 90A operation or 92A/B operation to allow for future use and system expansion.

2.	The OFF LED shall be Yellow, the ON LED shall be green, the Trouble/Fault LED shall be Amber/Orange for each switch. The Trouble/Fault indicator shall indicate a trouble in the control and/or monitor points associated with that switch. In addition, each group of eight switches shall have two LEDS and one momentary switch which allow the following functions: An Amber LED to indicate an OFF-NORMAL switch position, in the ON or OFF position; A Green LED to indicate ALL AUTO switch position; A Local Acknowledge/Lamp Test momentary switch.

3.	Each switch shall have the capability to monitor and control two addressable inputs and two addressable outputs. In all modes, the ON and OFF indicators shall continuously follow the device status not the switch position. Positive feedback shall be employed to verify correct operation of the device being controlled. Systems that indicate on/off/auto by physical switch position only are not acceptable.

4.	All HVAC switches (i.e., limit switches, vane switches, etc.) shall be provided and installed by the HVAC contractor.

5.	It shall be possible to meet the requirements mentioned above utilizing wall mounted custom graphic.

U.	SpectrAlert Advance Speakers

1.	The Speaker appliance shall be System Sensor SpectrAlert Advance model ______ Speaker. The speaker shall be listed to UL 1480 for Fire Protective Signaling Systems. It shall be a dual-voltage transformer speaker capable of operation at 25.0 or 70.7 nominal Vrms. The speaker shall have a frequency range of 400 to 4,000 Hz and shall have an operating temperature between 32°F and 120°F. It shall mount to a 4 x 4 x 2 1/8-inch back box.

2.	A universal mounting plate shall be used for mounting ceiling and wall speaker products. The notification appliance circuit and amplifier wiring shall terminate at the universal mounting plate.

3.	Speakers shall be plug-in and shall have the ability to check wiring continuity via a shorting spring on the universal mounting plate. The shorting spring shall also provide tamper resistance via an open circuit if the device is removed. Speaker design shall isolate speaker components to reduce ground fault incidents.

4.	The speaker shall have power taps (from ¼ watt to 2 watts) and voltage that are selected by rotary switches. All models shall have a maximum sound output of 86 dB at 10 feet and shall incorporate an open back construction.

5.	All notification appliances shall be backward compatible.

Ceiling Speaker			                 Wall Speaker

V.	SpectrAlert Advance Speaker Strobes

1.	The Speaker Strobe appliance shall be System Sensor SpectrAlert Advance model ______ Speaker Strobe. The speaker strobe shall be listed to UL 1971 and UL 1480 and be approved for fire protective signaling systems. It shall be a dual-voltage transformer speaker strobe capable of operation at 25.0 or 70.7 nominal Vrms. The speaker shall have a frequency range of 400 to 4,000 Hz and shall have an operating temperature between 32°F and 120°F. It shall mount to a 4 x 4 x 2 1/8-inch back box.

2.	A universal mounting plate shall be used for mounting ceiling and wall speaker strobe products. The notification appliance circuit and amplifier wiring shall terminate at the universal mounting plate.  Also, SpectrAlert Advance speaker strobes and the Sync•Circuit™ Module MDL3 accessory, if used, shall be powered from a non-coded notification appliance circuit output and shall operate on a nominal 12 or 24 volts (includes fire alarm panels with built in sync). When used with the Sync•Circuit Module MDL3, 12-volt rated notification appliance circuit outputs shall operate between 8.5 and 17.5 volts; 24-volt rated notification appliance circuit outputs shall operate between 16.5 to 33 volts. If the notification appliances are not UL 9th edition listed with the corresponding panel or power supply being used, then refer to the compatibility listing of the panel to determine maximum devices on a circuit.

3.	Speaker strobes shall be plug-in and shall have the ability to check wiring continuity via a shorting spring on the universal mounting plate. The shorting spring shall also provide tamper resistance via an open circuit if the device is removed. Speaker strobe design shall isolate speaker components to reduce ground fault incidents.

4.	The speaker strobe shall have power taps (from ¼ watt to 2 watts) and voltage that are selected by rotary switches. All models shall have a maximum sound output of 86 dB at 10 feet and shall incorporate an open back construction.  The strobe shall consist of a xenon flash tube with associated lens/reflector system and operate on either 12V or 24V. The strobe shall also feature selectable candela output, providing options for 15 or 15/75 candela when operating on 12V and 15, 15/75, 30, 75, 110, or 115 when operating on 24V. The strobe shall comply with NFPA 72 and the Americans with Disabilities Act requirement for visible signaling appliances, flashing at 1 Hz over the strobe’s entire operating voltage range.

5.	All notification appliances shall be backward compatible.

Ceiling Speaker Strobe		           Wall Speaker Strobe

6.	Strobe lights shall meet the requirements of the ADA, UL Standard 1971and be fully synchronized.

PART 3.0 - EXECUTION

3.1.	INSTALLATION:

A.	Installation shall be in accordance with the NEC, NFPA 72, local and state codes, as shown on the drawings, and as recommended by the major equipment manufacturer.

B.	All conduit, junction boxes, conduit supports and hangers shall be concealed in finished areas and may be exposed in unfinished areas. Smoke detectors shall not be installed prior to the system programming and test period. If construction is ongoing during this period, measures shall be taken to protect smoke detectors from contamination and physical damage.

C.	All fire detection and alarm system devices, control panels and remote annunciators shall be flush mounted when located in finished areas and may be surface mounted when located in unfinished areas.

D.	Manual fire alarm boxes shall be suitable for surface mounting or semi-flush mounting as shown on the plans, and shall be installed not less than 42 inches (1067 mm), nor more than 48 inches (122 mm) above the finished floor.

3.2.	TEST:

The service of a competent, factory-trained engineer or technician authorized by the manufacturer of the fire alarm equipment shall be provided to technically supervise and participate during all of the adjustments and tests for the system. All testing shall be in accordance with NFPA 72.

A.	Before energizing the cables and wires, check for correct connections and test for short circuits, ground faults, continuity, and insulation.

B.	Close each sprinkler system flow valve and verify proper supervisory alarm at the FACP.

C.	Verify activation of all waterflow switches.

D.	Open initiating device circuits and verify that the trouble signal actuates.

E.	Open and short signaling line circuits and verify that the trouble signal actuates.

F.	Open and short notification appliance circuits and verify that trouble signal actuates.

G.	Ground all circuits and verify response of trouble signals.

H.	Check presence and audibility of tone at all alarm notification devices.

I.	Check installation, supervision, and operation of all intelligent smoke detectors using the walk test.

J.	Each of the alarm conditions that the system is required to detect should be introduced on the system. Verify the proper receipt and the proper processing of the signal at the FACP and the correct activation of the control points.

K.	When the system is equipped with optional features, the manufacturer's manual shall be consulted to determine the proper testing procedures. This is intended to address such items as verifying controls performed by individually addressed or grouped devices, sensitivity monitoring, verification functionality and similar.

3.3.	FINAL INSPECTION:

A.	At the final inspection, a factory-trained representative of the manufacturer of the major equipment shall demonstrate that the system functions properly in every respect.

3.4.	INSTRUCTION:

A.	Instruction shall be provided as required for operating the system. Hands-on demonstrations of the operation of all system components and the entire system including program changes and functions shall be provided.

B.	The contractor and/or the systems manufacturer's representatives shall provide a typewritten "Sequence of Operation."

END OF SECTION