ENGINEERING SPECIFICATION

IP COMMUNICATOR

PART 1.0 - GENERAL

1.1	DESCRIPTION:

A.	This section of the specification includes the furnishing, installation, connection and testing of the IPDACT Communicator.

B. 	The IPDACT Communicator shall comply with requirements of NFPA Standard No. 72 for Other Transmission Technologies except as modified and supplemented by this specification.

C. 	The IPDACT Communicator shall be manufactured by an ISO 9001 certified company and meet the requirements of BS EN9001: ANSI/ASQC Q9001-1994.

D. 	The IPDACT Communicator shall be manufactured or supplied 100% by a single U.S. manufacturer (or division thereof).

E. 	Underwriters Laboratories Inc. (UL) – USA.

F. 	The installing company shall employ NICET (minimum Level II Fire Alarm Technology) technicians on site to guide the final check-out and to ensure the systems integrity.

G. 	The IPDACT Communicator shall meet requirements of UL ANSI 864 Ninth Edition.

1.2	SCOPE:

A. 	An intelligent, IPDACT Communicator shall be installed in accordance to the project specifications and drawings.

B.	Basic Performance:

1. 	The IPDACT Communicator connects directly to the primary and secondary analog UL Listed Fire Alarm Control Panel telephone ports.

2. 	Supports both dynamic (DHCP) or Public and Private Static IP addressing.

3.	Communicates over any type of customer-provided Ethernet 10/100 Base network connection (LAN or WAN), DSL modem or cable modem.

4.  	Data transmits over standard contact-ID protocol is secured with the industry’s highest level of encryption (AES 512 bit).

5.	Fast alarm transmission (less than 10 second transmission time).

6.	Supports dual-destination IP receiver address for high redundancy configurations: all signals are sent to a secondary address should the primary become unavailable.

7.	User programmable UDP ports.

8.	Supports an optional third maintenance Teldat Visoralarm receiver installed at the end user’s facility that permits local alarm monitoring. Alarms are received simultaneously at both the central station and the customer’s facility. A filter can be applied to annunciate specific alarm types such as trouble-only events.

9.	Supports upload/download using existing Fire Alarm Control Panel programming tools.

10. 	Two supervised inputs and two outputs

11.	 All circuits shall be power-limited, per UL864 requirements.

C. 	BASIC SYSTEM FUNCTIONAL OPERATION

1.	When a fire alarm condition (Alarm, Supervisory or Trouble) is detected, the Fire Alarm Panel will send Contact ID event information from its DACT port.

2.	The IP Communicator will sense the off-hook status of the panel and accept all data.

3.	The IP Communicator will then immediately packetize the Contact ID information into UDP protocol and encrypt it with 512 bits of AES encryption and send it to the central station. The central station receiver will decrypt and unpacketize the Contact ID information and present it to the central station automation software.

4.	Upon operator acknowledgement the kiss-off signal will be sent back to the panel.

1.3	SUBMITTALS

A.	General:

1. 	Two copies of all submittals shall be submitted to the Architect/Engineer for review.

2. 	All references to manufacturer's model numbers and other pertinent information herein is intended to establish minimum standards of performance, function and quality. Equivalent compatible UL-listed equipment from other manufacturers may be substituted for the specified equipment as long as the minimum standards are met.

3. 	For equipment other than that specified, the contractor shall supply proof that such substitute equipment equals or exceeds the features, functions, performance, and quality of the specified equipment.

B. 	Shop Drawings:

1. 	Sufficient information, clearly presented, shall be included to determine compliance with drawings and specifications.

2. 	Include manufacturer's name(s), model numbers, ratings, power requirements, equipment layout, complete wiring diagrams and conduit layouts.

C. 	Manuals:

1. 	Submit simultaneously with the shop drawings, complete operating and maintenance manuals listing the manufacturer's name(s), including technical data sheets.

2.	Wiring diagrams shall indicate internal wiring for IPDACT Communicator

and the interconnections between the items of equipment.

3. 	Provide a clear and concise description of operation that gives, in detail, the information required to properly operate the equipment and system.

D. 	Software Modifications

1. 	Provide the services of a qualified technician to perform all system software modifications, upgrades or changes.  Response time of the technician to the site shall not exceed 4 hours.

2. 	Provide all hardware, software, programming tools and documentation necessary to modify the IPDACT Communicator on site. The system structure and software shall place no limit on the type or extent of software modifications on-site.

1.4	GUARANTY:

A.	All work performed and all material and equipment furnished under this contract shall be free from defects and shall remain so for a period of at least one (1) year from the date of acceptance. The full cost of maintenance, labor and materials required to correct any defect during this one year period shall be included in the submittal bid.

1.5 	MAINTENANCE:

A. 	Maintenance and testing shall be on a semi-annual schedule or as required by the local AHJ. A preventive maintenance schedule shall be provided by the contractor describing the protocol for preventive maintenance.

B. 	As part of the bid/proposal, include a quote for a maintenance contract to provide all maintenance, tests, and repairs described below. Include also a quote for unscheduled maintenance/repairs, including hourly rates for technicians trained on this equipment and response travel costs for each year of the maintenance period.

C.	Submittals that do not identify all post contract maintenance costs will not be accepted. Rates and costs shall be valid for the period of five (5) years after expiration of the guaranty.

1.6 	POST CONTRACT EXPANSIONS:

A. 	The contractor shall have the ability to provide parts and labor to expand the system specified, if so requested, for a period of five (5) years from the date of acceptance.

B. 	Submittals that do not include this estimate of post contract expansion cost will not be accepted.

1.7 	APPLICABLE STANDARDS AND SPECIFICATIONS:

A.	The specifications and standards listed below form a part of this specification. The system shall fully comply with the latest issue of these standards, if applicable.

B.	 National Fire Protection Association (NFPA) - USA:

1.	No. 13	Sprinkler Systems

2.	No. 70	National Electric Code (NEC)

3.	No. 72	National Fire Alarm Code

4.	No. 101 	Life Safety Code

5. 	No. 38	Manually Actuated Signaling Boxes

6.      No. 217 	Smoke Detectors, Single and Multiple Station

7. 	No. 228 	Door Closers–Holders for Fire Protective Signaling Systems

8.	No. 268 Smoke Detectors for Fire Protective Signaling Systems

9.	No. 268A Smoke Detectors for Duct Applications

10.	No. 346 Waterflow Indicators for Fire Protective Signaling Systems

11.	No. 464 Audible Signaling Appliances

12.	No. 521 Heat Detectors for Fire Protective Signaling Systems

13.	No. 864 Control Units for Fire Protective Signaling Systems

14.	No. 1481 Power Supplies for Fire Protective Signaling Systems

15.    No. 1610 Central Station Burglar Alarm Units

16.    No. 1638 Visual Signaling Appliances

17.	No. 1971 Visual Signaling Appliances

18.    No. 2017    General-Purpose Signaling Devices and Systems

19     CAN/ULC     S524-01 Standard for Installation of Fire Alarm Systems

20.	The IPDACT Communicator shall be ANSI 864, 9th Edition Listed.

B. 	The system and its components shall be Underwriters Laboratories, Inc. listed under the appropriate UL testing standard as listed herein for fire alarm applications and the installation shall be in compliance with the UL listing.

C. 	Local and State Building Codes.

D.	All requirements of the Authority Having Jurisdiction (AHJ).

1.8 	APPROVALS:

A. 	The system shall have proper listing and/or approval from the following nationally recognized agencies:

1.	UL	Underwriters Laboratories Inc

2.	CSFM	California State Fire Marshal

PART 2.0 	PRODUCTS

2.1 	EQUIPMENT AND MATERIAL, GENERAL:

A.	 All equipment and components shall be new, and the manufacturer's current model. The materials, appliances, equipment and devices shall be tested and listed by a nationally recognized approvals agency for use as part of a fire protective signaling system, meeting the National Fire Alarm Code.

B. 	All equipment and components shall be installed in strict compliance with manufacturers' recommendations. Consult the manufacturer's installation manuals for all wiring diagrams, schematics, physical equipment sizes, etc., before beginning system installation.

2.2 	CONDUIT AND WIRE:

A. 	Conduit:

1. 	Conduit shall be in accordance with The National Electrical Code (NEC), local and state requirements.

2. 	Where required, all wiring shall be installed in conduit or raceway.  Conduit fill shall not exceed 40 percent of interior cross sectional area where three or more cables are contained within a single conduit.

3. 	Cable must be separated from any open conductors of power, or Class 1 circuits, and shall not be placed in any conduit, junction box or raceway containing these conductors, per NEC Article 760.

4. 	Conduit shall not enter the fire alarm control panel, or any other remotely mounted control panel equipment or backboxes, except where conduit entry is specified by the Fire Alarm Control Panel manufacturer.

5. 	Conduit shall be 3/4 inch (19.1 mm) minimum.

B. 	Wire:

1. 	All IPDACT Communicator wiring shall be new.

2. 	Wiring shall be in accordance with local, state and national codes (e.g., NEC Article 760) and as recommended by the manufacturer of the IPDACT Communicator.

3. 	All wire and cable shall be listed and/or approved by a recognized testing agency for use with a protective signaling system.

4. 	Wire and cable not installed in conduit shall have a fire resistance rating suitable for the installation as indicated in NEC 760 (e.g., FPLR).

5. 	All field wiring (with exception of external communications Ethernet) shall be electrically supervised for open circuit and ground fault.

C. 	Terminal Boxes, Junction Boxes and Cabinets:

1.	All boxes and cabinets shall be UL listed for their use and purpose.

2.3 	IP COMMUNICATOR:

A.	The IPDACT Communicator shall be a NOTIFIER Model IPDACT-2 or IPDACT-2UD (Upload/Download). Central station supervisory equipment shall be a Teldat Corporation Visoralarm-Plus 2U listed to UL-864 standards.

B.	IPDACT Communicator module is connected to the on board DACT, the system shall be capable of transmitting Contact ID formatted alarms, supervisory or troubles to a central station equipped with a compatible IP receiver via Ethernet over a private or public WAN/LAN, Intranet or Ethernet.

C. 	System Capacity and General Operation

1. 	The IPDACT Communicator shall be an integral module component of the fire alarm control panel enclosure.

2. 	The IPDACT Communicator shall include connections to the alarm panel’s phone outputs and shall convert the contact ID protocol in DTMF form into UDP Ethernet Packets. It shall include the ability for simultaneous reporting of panel events up to three different IP addresses.

3. 	The IPDACT Communicator shall be completely field-programmable locally from a PC via a serial port or via Ethernet and Telnet.

4. 	The IPDACT Communicator shall be capable of transmitting events in contact ID format.

5. 	Communication shall include vital system status such as:

a.	Independent Zone (Alarm, trouble, non-alarm, supervisory)

b.	Independent Addressable Device Status

c.	AC (Mains) Power Loss

d.	Low Battery and Earth Fault

e.	System Off Normal

f.	12 and 24 Hour Test Signal

g.	Abnormal Test Signal (per UL requirements)

h.	EIA-485 Communications Failure

i.	IP Line Failure

6. 	The IPDACT Communicator shall support independent zone/point reporting via the Contact ID format. In this format, the IPDACT shall support the transmission of addressable points within the system. This format shall enable the central station to have exact details concerning the location of the fire for emergency response.  The IPDACT Communicator shall be capable of providing simulated phone lines to the IPDACT Communicator and panel communication over IP shall be transparent to the panel’s normal operation over phone lines.

7. 	The IPDACT Communicator shall utilize a supervisory heart beat signal of no less than once every 90 seconds insuring multiplexed level line supervision.

8.	Loss of Internet or Intranet connectivity shall be reported in no more than 200 seconds.

9. 	Alarm events shall be transmitted to a central station in no less than 90 seconds from time of initiation to time of notification.

10. 	The supervising station shall consist of a Teldat Corporation Visoralarm-Plus 2U receiver.  Said receiver shall contain a smart card for backup of all account data.

11.	Backup smart card shall initiate a new receiver with all account information in less than 60 seconds from power up.

D. 	Enclosures:

1.	The IPDACT Communicator shall be housed in a UL-listed cabinet.

2. 	The back box and door shall be constructed of steel with provisions for electrical conduit connections into the sides and top.

E. 	Power Supply:

1. 	The main power supply shall operate on 120 VAC, 60 Hz, and shall provide all necessary power for the IPDACT Communicator.

2.	Positive-Temperature-Coefficient (PTC) thermistors, circuit breakers, or other over-current protection shall be provided on all power outputs. The power supply shall provide an integral battery charger or may be used with an external battery and charger systems. Battery arrangement may be configured in the field.

3. 	The main power supply shall continuously monitor all field wires for earth ground conditions.

2.4 	BATTERIES:

A.	Upon loss of Primary (AC) power to the IPDACT Communicator, the batteries shall have sufficient capacity to power the IPDACT Communicator for required standby time (24 or 60 hours) followed by 5 minutes of alarm.

B. 	The batteries are to be completely maintenance free. No liquids are required. Fluid level checks for refilling, spills, and leakage shall not be required.

C. 	If necessary to meet standby requirements, external battery/charger systems may be used.

PART 3.0 	EXECUTION

3.1 	INSTALLATION:

A. 	Installation shall be in accordance with the NEC, NFPA 72, local and state codes, as shown on the drawings, and as recommended by the major equipment manufacturer.

B. 	All conduit, junction boxes, conduit supports and hangers shall be concealed in finished areas and may be exposed in unfinished areas.

3.2 	TEST:

A.	The service of a competent, NICET level II technician shall be provided to technically supervise and participate during all of the adjustments and tests for the system. All testing shall be in accordance with NFPA 72.

B. 	Before energizing the cables and wires, check for correct connections and test for short circuits, ground faults, continuity, and insulation.

3.3 	FINAL INSPECTION:

A. 	At the final inspection, a minimum NICET Level II technician shall demonstrate that the system functions properly in every respect.

3.4 	INSTRUCTION:

A. 	Instruction shall be provided as required for operating the system. Hands-on demonstrations of the operation of all system components and the entire system including program changes and functions shall be provided.

B. 	The contractor or installing dealer shall provide a user manual indicating "Sequence of Operation."

END OF SECTION