NOTIFIER INSPIRE SPECIFICATION- N16x

Fire Detection and Alarm specifications are highly customizable based on project requirements. This version has been created considering most used scenarios for Large Projects

| Selections | Large Projects N16x |
| --- | --- |
| New Project or Retrofits | New |
| Networking | Yes |
| Voice | Yes |
| Amplifiers | Distributed Amplifiers, Bulk Digital Amplifiers |
| Network Type | High Speed |
| Media Type | Multi Mode |
| Notification Wall/Ceiling Appliance color | White |
| Releasing | Yes |
| Lamp Drive Module | Yes |
| CLSS | Yes |
| VESDA | Yes |
| Self Test | Yes |
| Wireless | No |
| Chimes | No |
| Graphical Workstation | Yes |

For project specific customization, SpecLink Cloud subscribers may use “284600-HWNOT2- Fire Detection and Alarm- NOTIFIER INSPIRE” on SpecLink Cloud or contact  the Honeywell Fire Application Engineering team at FAE.Fire@Honeywell.com

- Section 284600 
Fire Detection and Alarm - Notifier INSPIRE

PART 1  GENERAL

Related Requirements

Section 078400 - Firestopping.

Section 260526 - Grounding and Bonding for Electrical Systems.

Section 260548 - Vibration and Seismic Controls for Electrical Systems:  Requirements for seismic qualification of equipment specified in this section.

Section 260553 - Identification for Electrical Systems:  Identification products and requirements.

Abbreviations and Acronyms

A:  Amps.

AHJ:  Authorities having jurisdiction.

AV:  Audio-visual.

CLSS:  Connected life-safety services.

EVACS:  Emergency voice/alarm communication systems.

FACU:  Fire alarm control unit.

HVAC:  Heating, ventilation, and air conditioning.

IDC:  Initiating device circuit.

LAN:  Local area network.

NAC:  Notification appliance circuit.

SLC:  Signaling line circuit.

USB:  Universal serial bus.

VAC:  Voltage alternating-current.

VDC:  Voltage direct-current.

Vrms:  Voltage root-mean-square.

W:  Watts.

Reference Standards

ADA Standards - 2010 ADA Standards for Accessible Design; 2010.

FM (AG) - FM Approval Guide; Current Edition.

ISO 9001 - Quality Management Systems — Requirements; 2015, with Amendment (2024).

NECA 1 - Standard for Good Workmanship in Electrical Construction; 2023.

NFPA 10 - Standard for Portable Fire Extinguishers; 2022.

NFPA 25 - Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems; 2023.

      - NFPA 70 - National Electrical Code; Most Recent Edition Adopted by Authority Having Jurisdiction, Including All Applicable Amendments and Supplements.

      - NFPA 72 - National Fire Alarm and Signaling Code; Most Recent Edition Cited by Referring Code or Reference Standard.

NFPA 76 - Standard for the Fire Protection of Telecommunications Facilities; 2020.

NFPA 2001 - Standard on Clean Agent Fire Extinguishing Systems; 2022, with Errata.

UL 38 - Standard for Manual Signaling Boxes for Fire Alarm Systems; Current Edition, Including All Revisions.

UL 268 - Standard for Smoke Detectors for Fire Alarm Systems; Current Edition, Including All Revisions.

UL 268A - Standard for Smoke Detectors for Duct Application; Current Edition, Including All Revisions.

UL 294 - Access Control System Units; Current Edition, Including All Revisions.

UL 464 - Standard for Audible Signaling Devices for Fire Alarm and Signaling Systems, Including Accessories; Current Edition, Including All Revisions.

UL 521 - Standard for Heat Detectors for Fire Protective Signaling Systems; Current Edition, Including All Revisions.

      - UL 864 - Control Units and Accessories for Fire Alarm Systems; Current Edition, Including All Revisions.

UL 1076 - Proprietary Burglar Alarm Units and Systems; Current Edition, Including All Revisions.

UL 1449 - Standard for Surge Protective Devices; Current Edition, Including All Revisions.

UL 1480 - Standard for Speakers for Fire Alarm and Signaling Systems, Including Accessories; Current Edition, Including All Revisions.

UL 1481 - Power Supplies for Fire-Protective Signaling Systems; Current Edition, Including All Revisions.

UL 1638 - Standard for Visible Signaling Devices for Fire Alarm and Signaling Systems, Including Accessories; Current Edition, Including All Revisions.

UL 1711 - Amplifiers for Fire Protective Signaling Systems; Current Edition, Including All Revisions.

UL 1971 - Standard for Signaling Devices for the Hearing Impaired; Current Edition, Including All Revisions.

UL 2017 - General-Purpose Signaling Devices and Systems; Current Edition, Including All Revisions.

UL 2075 - Standard for Gas and Vapor Detectors and Sensors; Current Edition, Including All Revisions.

UL 2610 - Commercial Premises Security Alarm Units and Systems; Current Edition, Including All Revisions.

UL 60950-1 - Information Technology Equipment – Safety – Part 1: General Requirements; Current Edition, Including All Revisions.

Administrative Requirements

Coordination:

Coordinate arrangement of equipment with dimensions and clearance requirements of actual equipment to be installed.

Coordinate placement of devices and notification appliances with potential conflicts and view obstructions installed under other sections or by others.

Coordinate work to provide power for equipment at required locations.

Municipal Alarm Connections:  Coordinate requirements for connection with municipality representative.

Notify Engineer of conflicts with or deviations from Contract Documents. Obtain direction before proceeding with work.

Preinstallation Meetings:

Conduct meeting with facility representative to review devices, notification appliances, and equipment locations.

Conduct meeting with facility representative and other related equipment manufacturers to discuss fire alarm system interface requirements.

Sequencing:

Do not install devices or notification appliances until final surface finishes and painting are complete.

Submittals

See Section 013000 - Administrative Requirements for submittal procedures.

Include sufficient information, clearly presented, to determine compliance with specifications and drawings.

Bill of Material - Indicate the following for each component of system:

Quantity.

Model number.

Description.

Submittal Documents:

Prepare and submit information required for plan review and permitting by AHJ, including but not limited to floor plans, details, and calculations.

Product Data:  Provide manufacturer's standard catalog pages and data sheets for products, including ratings, configurations, standard wiring diagrams, dimensions, finishes, service condition requirements, and installed features.

Shop Drawings:

Comply with NFPA 72 chapter "Documentation," including noting names of installers, Owner(s), and system classification type information.

Include plan views, drawn to identified scale, noting locations of fire alarm components and associated building or system coordination, as required by NFPA 72.

Include elevations and details of proposed equipment arrangements.

Include system interconnection schematic riser diagram showing proposed and approved cable size and type; coordinated with floor plans and describing circuit class, survivability, and application specific information required by NFPA 72.

Include typical wiring diagrams for devices, notification appliances, remote indicators, annunciators, remote test stations, and end-of-line and power supervisory devices.

Include requirements and control unit diagrams for interfacing with other systems.

Indicate system zone boundaries.

Include narrative description sequence of operation with input/output matrix.

Control Panel:  Provide sheet that details exterior and interior views of control panel and clearly shows associated wiring information.

Custom Graphic Annunciators:  Include proof for approval prior to fabrication.

Air-Sampling Smoke Detection Systems:  Include air-sampling pipe network layout with sampling ports identified.

Circuit Calculations:

Provide NAC ampacity and voltage drop calculations.

Include spare capacity calculations.

EVACS:  Provide speaker circuit dB loss calculations for each speaker circuit.

Include spare capacity calculations.

Provide standby battery calculations.

Include spare capacity calculations.

Air Sampling Smoke Detection Systems:  Include calculations demonstrating compliance with specified requirements.

Manufacturer's equipment seismic qualification certification.

Evidence of installer name and state license number with expiration date.

Inspection and Test Reports:

Installer to submit inspection and test plan prior to closeout demonstration.

Installer to submit NFPA 72 "Record of Inspection and Testing" forms, stored in cloud based service and available via web browser or file download.

Installer to submit NFPA 72 "Record of Completion" forms, digitally signed by Owner and authorized representative of AHJ, stored in cloud based service and available via web browser or file download.

Operation and Maintenance Data:

Include detailed information on system operation, equipment programming and setup.

Include manufacturer's preventive maintenance recommendations.

Other data as defined in NFPA 72 chapter "Inspection, Testing, and Maintenance."

Include contact information for entity that will be providing contract maintenance and trouble call-back service.

Maintenance contracts.

Project Record Documents:

Installer to record actual locations of system components and installed wiring arrangements and routing. Indicate final devices, notification appliances, and terminal identifications.

Indicate actual programmed operating sequences, including control events by device, updated input/output matrix, and voice messages by event or printed copy of program.

Place in as-built documents cabinets.

Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

Extra Spot-Type Detectors:  Five percent of total quantity installed for each type, but not less than one of each type supplied.

Extra Notification Appliances:  Five percent of total quantity installed for each type, but not less than one of each type supplied.

Extra Addressable Modules:  One of each type supplied.

Extra Fuses:  Two of each size and type; store inside applicable control cabinet.

Software:  One copy of software not resident in read-only memory.

Quality Assurance

Comply with the following:

Applicable local codes.

ADA Standards.

NFPA 70 (National Electrical Code)​ 2023​.

NFPA 72 (National Fire Alarm and Signaling Code)​ 2022​.

Equipment, Programming, and Installation Supervision:

Provide services of approved engineered systems distributor of Honeywell Notifier for equipment, programming, and installation supervision.

Software Modifications:

Provide services of Honeywell Notifier factory-trained and authorized technician to perform system software modifications, upgrades, or changes.

Provide use of hardware, software, programming tools, and documentation necessary to modify fire alarm system software on-site.

Modification includes addition and deletion of devices, circuits, zones, and changes to system operation and custom label changes for devices or zones.

System structure and software without limits on type or extent of software modifications on-site.

Modification of software maintains system power without loss of system fire alarm system while modifications are being made.

Manufacturer Qualifications:  Company specializing in manufacturing products specified in this section with minimum three years documented experience.

Authorized support facilities located within 50 miles (80 km) of project site.

Installer Qualifications:

Company with minimum three years documented experience with similar fire alarm systems and providing contract maintenance service as regular part of their business.

Familiar with products to be installed through documented manufacturer training, authorization, or equivalent demonstrated experience.

Notifier Basis of Design System:  Specialized training as provided by Notifier Premier representative.

Installer Personnel:  At least three years experience installing fire alarm systems.

Supervisor:  State licensed and NICET Level III certified fire alarm technician.

Contract maintenance office located within 50 miles (80 km) of project site.

Licensed electrical or systems contractor in the State in which the Project is located.

Product Evaluation and Listing Organization Qualifications:  Organization engaged in evaluation of products and services, including those recognized by OSHA as Nationally Recognized Testing Laboratory (NRTL), and acceptable to AHJ.

Delivery, Storage, and Handling

Receive, inspect, handle, and store products in accordance with manufacturer's instructions.

Store products in manufacturer's unopened packaging, keep dry and protect from damage until ready for installation.

Protect materials from damage during handling and installation.

Field Conditions

Maintain field conditions within manufacturer's required service conditions during and after installation.

Warranty

See Section 017800 - Closeout Submittals for additional warranty requirements.

Provide minimum three year manufacturer warranty for FACU and accessory equipment covering repair or replacement due to defective materials or workmanship.

PART 2  PRODUCTS

Manufacturers

Fire Alarm Control Unit and Accessory Equipment - Basis of Design:  Notifier INSPIRE Series by Honeywell;  www.securityandfire.honeywell.com/notifier/en-us/browseallcategories/control-panel/notifier-inspire-series/#sle.

Source Limitations:  Where possible, furnish system components and accessories produced by one manufacturer and obtained from one supplier.

Fire Alarm System

Provide new fire alarm system consisting of required components (e.g., equipment, conduit, boxes, wiring, connectors, hardware, supports, accessories, software, and system programming) as necessary for complete operating system that provides functional intent indicated.

Products:  Listed, classified, and labeled as suitable for purpose intended.

Power Sources:

Primary:  Dedicated branch circuits from facility power distribution system.

Secondary:  Storage batteries with capacity to operate system for period specified by NFPA 72.

Battery Storage Capacity:

Provide standby (nonalarm) operation sufficient for 24 hours.

Provide additional alarm operation for 15 minutes.

Calculate combined of standby load plus alarm load for overall battery storage capacity requirements, per power supply.

Provide 25 percent additional overall battery capacity correction factor.

Provide 20 percent spare battery capacity.

Spare Circuit Capacity:

SLCs:  Minimum 25 percent spare capacity.

NACs:  Minimum 25 percent spare capacity.

Speaker Circuits:  Minimum 25 percent spare capacity.

Exterior Notification:  In addition to required occupant notification, provide notification appliances on exterior of building.

General Wiring Methods:

Pathway class designations and pathway survivability are as defined in NFPA 72.

Pathway Class Designations:

Unless otherwise indicated or required, pathways to meet the following requirements:

SLCs:  Class B.

IDCs:  Class B.

NACs:  Class B.

Network Communications:  Class B.

Other Wiring:

Other life safety control features not covered above (e.g., door holder circuits, elevator recall circuits, fire smoke dampers, and air handling system interfaces), wired as Class D.

Where Class D wiring is not possible due to limitation of equipment, wiring to be limited to 3 feet (910 mm) between addressable control module and equipment and be installed in metal conduit.

Exceptions:

SLCs for _________:  Class B.

IDCs for _________:  Class B.

NACs for _________:  Class B.

Network Communications for _________:  Class B.

Pathway Survivability:

Unless otherwise indicated or required, pathways to meet requirements for Pathway Survivability Level 0.

Rated cable to be one of the following in accordance with NFPA 72:

Two-hour fire-rated circuit integrity (CI) or fire-resistive cable.

Two-hour fire-rated cable system (mineral insulated cable).

Two-hour fire-rated enclosure or protected area.

Performance alternative approved by AHJ.

Seismic Qualification:  Provide fire alarm system and associated components suitable for application under project seismic design criteria where required. Include certification of compliance with submittals.

Fire Alarm System Interfaces:

UL 864 listed unless otherwise indicated.

Descriptions below are intended to provide means for interface. See project sequence of operations, narrative, and input/output matrix for execution requirements.

Provide addressable monitor modules as indicated or as required for connection to addressable FACU. Unless devices are explicitly permitted to be connected together as one zone, provide separate addressable monitoring points for each device to be individually identifiable by addressable FACU.

Provide addressable relay module as indicated or as required to perform necessary functions via dry-contact interface. Where load exceeds module contact rating, provide accessory power isolation relays suitable for load as required.

Fire Sprinkler Systems:

Waterflow Switches:  Provide minimum of one monitoring point input per switch.

Control Valve Supervisory (Tamper) Switches:  Provide minimum of one monitoring point input per switch.

PIV (Post Indicator Valve) or Main Gate Valves:  Provide minimum of one monitoring point per switch.

Pressure Supervisory (High/Low Pressure) Switches:  Provide minimum of two monitoring point inputs per switch (separate points for high/low pressure signals).

Fire Pumps:  Provide minimum of four monitoring point inputs.

Preaction Control Panels:  Provide minimum of four monitoring point inputs per system.

Heat Trace (Freeze Protection) Monitoring Systems:  Provide minimum of two monitoring point inputs per system.

Freeze Protection:  For each sprinkler riser location, provide room temperature sensor to provide supervisory signal to FACU.

Fire Suppression Systems:

Releasing Service by FACU:

FACU to be listed for releasing service.

Provide addressable releasing control modules as indicated or as required for control of solenoids listed for releasing applications.

Provide manual releasing stations for suppression system activation as indicated.

Provide alarm bells for audible notification as indicated. Interface to dedicated NAC or addressable control module, 24 VDC, supervised. Default operation to be march time pattern on activation of first event, continuous tone on release.

Provide strobes for visible notification as indicated. Interface to dedicated NAC or addressable control module, 24 VDC, supervised. Default operation to be flash on activation of first event, flash on release.

Provide abort switches as indicated.

Emergency Responder Communication Enhancement System (ERCES):

Provide minimum of six monitoring point inputs per system.

Generator Systems:

Provide minimum of three monitoring point inputs per system.

Aviation Warning Light Systems:

Provide minimum of two monitoring point inputs per system.

Elevators:

Elevator Emergency Recall Operation:

In each elevator machine room, provide interface for each elevator car or group of elevator cars as determined by AHJ via separate addressable relay modules for each output signal below, where applicable.

Recall elevator to designated (primary) level.

Recall elevator to alternate level.

Smoke detection in elevator machine room (fire fighter's hat light).

Hoistway ventilation control.

Elevator power shutdown.

Escalators:

Escalator Shutoff:

For each escalator, provide output signal to stop escalator via addressable relay module and power isolation relay.

Fire and Smoke Doors/Shutters/Curtains:

Electromagnetic Door Holder Release:

Provide output signal for release of electromagnetic door holders via addressable relay module and power isolation relay.

Door holders powered via 24 VDC unless otherwise indicated.

Automatic Fire and Smoke Door/Shutter/Curtain Release:

Provide output signal for release of fire and smoke doors/shutters/curtains via addressable relay module and power isolation relay.

Unless otherwise indicated, door/shutter/curtain release activated as determined by AHJ.

Access-Controlled Doors:

Door Release:

Provide output signal for release of electrically locked doors via addressable relay module and power isolation relay.

Provide connection to UL 864 listed control system interface or interface with door control power where interruption of control power releases doors.

Access-controlled door release activated ​as determined by AHJ​.

Large-Diameter Industrial Paddle Fans:

Fan Shutoff:

Provide output signal to stop fans via addressable relay module and power isolation relay.

Fan shutoff activated as determined by AHJ.

Lighting/Dimming Control Systems:

System Override:

Provide output signal to override lighting/dimming controls via addressable relay module and power isolation relay.

Provide connection to UL 864 listed control system interface or interface with system control power where interruption of control power overrides system.

Sound and Audio/Visual Media Control Systems:

System Override:

Provide output signal to override sound and audio/visual media controls via addressable relay module and power isolation relay.

Provide connection to UL 864 listed system interface or interface with system control power where interruption of control power overrides system.

HVAC Systems:

Air Handling Units (AHUs) and Roof Top Units (RTUs):

Provide duct smoke detector on supply side of air stream for units over 2,000 cfm.

Provide duct smoke detector on return side of air stream for units over 15,000 cfm.

Provide remote test station for each duct smoke detector unless explicitly indicated as not required.

Provide output signal to shut down units with at least one duct smoke detector via addressable relay module.

Where fire/smoke dampers are located downstream of unit, provide monitoring point input to determine that unit is not operational and subsequently provide output signal to close such dampers via addressable relay module and power isolation relay.

Energy Recovery Units (ERUs):

Provide duct smoke detector on supply side of air stream.

Provide duct smoke detector on return side of air stream.

Provide remote test station for each duct smoke detector unless explicitly indicated as not required.

Provide output signal to shut down units with at least one duct smoke detector via addressable relay module.

Where fire/smoke dampers are located downstream of unit, provide monitoring point input to determine that unit is not operational and subsequently provide output signal to close such dampers via addressable relay module and power isolation relay.

Fire/Smoke Dampers:

Provide output signal to close fire/smoke damper via addressable relay module and power isolation relay.

Fire/smoke damper activated ​as determined by AHJ​.

By addressable duct smoke detector as specified in this section.

By conventional duct smoke detector furnished with fire/smoke damper (along with remote test station) as specified in other sections; provide addressable monitor module.

By corridor smoke detection, where fire/smoke dampers serve only corridors provided with smoke detection throughout and all dampers serving such corridor are activated.

By smoke detector installed within 5 feet (1.5 m) of fire/smoke damper air diffuser (in lieu of duct smoke detection), where fire/smoke dampers serve spaces other than corridors or corridors not provided with smoke detection; smoke detectors installed solely for activation of fire/smoke damper programmed as supervisory signal (not alarm) unless otherwise required by AHJ.

- --CHOOSE ONE OF THE FOLLOWING THREE PARAGRAPHS FOR POST-FIRE SMOKE REMOVAL SYSTEM--

Post-Fire Smoke Removal System - Dedicated, with Control by Fire Alarm System:

Fans Used for Post-Fire Smoke Removal:

Provide interface for the following output signals via addressable relay module and power isolation relay:

Open shaft isolation damper.

Start fan.

Provide interface for the following monitoring point inputs:

Confirmation of shaft isolation damper open status.

Confirmation of fan operating status.

Post-Fire Smoke Removal System - Nondedicated, with Control by Fire Alarm System:

Exhaust Fans, Supply Fans, and Energy Recovery Units (ERUs):  Interface with building automation system (BAS).

Fire/Smoke Dampers Also Used for Post-Fire Smoke Removal:  Interface with fire alarm system as indicated under "Fire/Smoke Dampers" in this article above, but also provide monitoring point input to confirm open status of damper.

Provide the following output signals and monitoring point inputs at FACU for interface with building automation system:

One relay output per floor of building covered by post-fire smoke removal system.

One monitor input per floor of building covered by post-fire smoke removal system.

One relay output for building general alarm condition.

Five relay outputs for spare signals.

Five monitor inputs for spare signals.

Post-Fire Smoke Removal System - Nondedicated, with Control by Building Automation System:

Exhaust Fans, Supply Fans, and Energy Recovery Units (ERUs):  Interface with building automation system (BAS).

Fire/Smoke Dampers Also Used for Post-Fire Smoke Removal:  Interface with fire alarm system as indicated under "Fire/Smoke Dampers" in this article above, but also provide monitoring point to confirm open status of damper.

Provide the following output signals and monitoring point inputs at FACU for interface with building automation system:

One relay output per floor of building covered by post-fire smoke removal system.

One relay output per exhaust fan, supply fan, and ERU used for post-fire smoke removal, in order to send signal to BAS to place fan into post-fire smoke removal mode.

One monitor input per exhaust fan, supply fan, and ERU used for post-fire smoke removal, in order to receive signal from BAS that fan has been placed into post-fire smoke removal mode.

One relay output for building general alarm condition.

Five relay outputs for spare signals.

Five monitor inputs for spare signals.

Units with Sleeping Areas:

Devices Within Units:

Use fire alarm system-connected addressable devices for local unit detection/alarm (in lieu of single- and multiple-station alarms) and for building fire alarm event notification.

Local Unit Detection/Alarm:

Provide low frequency sounder bases for detectors (smoke and carbon monoxide as indicated).

Smoke Detector Activation:

Provide dedicated local unit supervisory signal to fire alarm system (separate from carbon monoxide detection).

Activate low-frequency sounder bases within same unit to provide NFPA 72-compliant temporal 3 pattern.

Detector Restoration:  Device activation to automatically restore to normal condition when smoke chamber obscuration levels drop below activation threshold.

Carbon Monoxide Detector Activation:

Provide dedicated local unit carbon monoxide supervisory signal to fire alarm system (separate from smoke detection).

Activate low-frequency sounder bases within same unit to provide NFPA 72-compliant temporal 4 pattern.

Detector Restoration:  Device activation to latch and only restore to normal condition upon reset command from FACU.

Hearing-Impaired Units:

Provide strobe (either in combination with sounder or separate device) in each legally-defined bedroom (177 cd), each living area (minimum 75 cd), and each bathroom (minimum 75 cd). Interface to dedicated NAC or addressable control module, 24 VDC, supervised.

Where unit includes both smoke and carbon monoxide detection, provide strobe labeled "ALERT" in lieu of "FIRE."

Synchronize notification appliances (sounders and strobes) within unit with each other.

Exclude local unit detection/alarm from any fire alarm system bypass/disable operation.

Building Fire Alarm Event Notification:

Provide low frequency sounders in each unit as indicated and as required to achieve minimum of 75 dB at pillow in legally-defined bedrooms and 15 dB over ambient in other interior areas of unit.

In lieu of providing separate low frequency sounders, system may activate detector low frequency sounder bases provided under local unit detection/alarm above.

Hearing-Impaired Units:  Use strobe provided for local unit detection/alarm above.

Synchronize notification appliances (sounders and strobes) within unit with each other and with common area notification appliances on same floor.

FACU to control activation mapping, silencing, and restoration.

Fire Alarm Control Unit and Related Equipment

Provide system listed and labeled as complying with agency listings and approval requirements as follows:

UL 864 (Control Units and Accessories for Fire Alarm Systems).

UL 2017 (General-Purpose Signaling Devices and Systems).

UL 2610 (Commercial Premises Security Alarm Units and Systems).

FM (AG) (FM approved).

City of Chicago.

Fire Department of New York (FDNY).

California State Fire Marshall (CSFM).

Provide cabinets and enclosures as indicated or as required to house system components.

Fire Alarm Control Unit (FACU):

SLCs:

Expandable enclosure, up to ten SLCs.

Supporting up to 3180 devices (1590 detectors and 1590 modules) configurable for Class B or Class A with signaling loop modules.

Configured with ​with voice and networking​ capability.

FACU User-Interface:

Provide high-definition 10-inch (254 mm) 1024 X 600 color touchscreen display.

Include audible and visible feedback with adjustable brightness solid-state LCD.

Include graphical QWERTY-style keypad on color, touchscreen display when alfa-numeric input is required.

Provide capability to scroll events by type using touchscreen (e.g., fire alarm, supervisory alarm, and trouble).

Permit uploading of custom background image.

Include ability to display up to 3,000 events in order of priority and time of occurrence.

Provide event counters to indicate total number of events by type.

Passwords and Users:

Support five access levels (e.g., system operator, building maintenance user, technician user, admin user, master user) and up to 50 usernames and passwords.

Each role level access has default customizable permissions.

Only master password allows password change.

Custom Actions:

Messages:  Provide means of entering up to 100 custom action messages, up to 160 characters each, with ability to assign any of 100 messages to any point.

Button:  Support up to 32 programmable custom action buttons on LCD touchscreen display used to enable/disable or control outputs without use of additional hardware.

Support up to ten remote LCD displays. See "Remote LCD Display" below.

Support display of events, from up to two additional nodes, without additional hardware or licensing.

Capable of displaying of all network events if configured as network control display, without additional hardware.

Provide FACU based on licensing model to allow for future expansion.

Support licensable features to expand logical operations and features for FACU and display functionality.

Support SLC expansion from one up to ten, using same FACU central processing unit and without need to be replaced or upgraded.

Online, Offline, or Remote Programming:

Provide means to program panel either through offline software utility program nonlocal to panel or connected online remotely via secured gateway.

Support upload/download of programmed database to personal computer (PC) or cloud storage.

History Events:

Support software maintained history file for last 10,000 events; each with time and date stamp with ability to scroll through stored events.

Include alarms, troubles, operator actions, and programming entries.

Provide ability to filter and sort history by event type, date, or point range.

Service Mode:

Provide ability to remotely access FACU for programming, testing, and control.

Include customizable time-out feature.

Trouble condition is displayed while in this mode.

Support AV magnet test with compatible AV appliances. Provide ability to test individual AV appliances on NAC by applying magnet to appliance momentarily; test does not activate entire circuit, minimizing disruptions during testing and inspection.

Support self-testing detector capability.

Logical Operators:

Support logical functions, including at minimum:  AND (ALL), OR (ANY), NOT, ONLY1, COUNT (one-nine), and TIMERS.

Inputs for Operators:  Time of day, addressable devices, software points, and trouble codes.

Capable of differentiating operator inputs by specific device status (i.e., fire alarm, prealarm, nonalarm, disable, supervisory, and security).

Releasing Service via Addressable Releasing Control Modules:

Agent Releasing:

FACU to be capable of supporting 50 releasing zones for independent hazards, with each zone capable of three cross-zone and four abort options; provide adjustable delay and discharge timers.

Water Releasing:

FACU support for 100 water releasing zones.

Up to 10 input sources either local panel or across fire alarm network.

Addressable Releasing Control Modules:  See "Addressable Modules" in this article below.

Manual Release Station:  See "Manual Pull Stations" under "Fire Alarm System Initiating Devices" article below.

Bells and Strobes:  See "Fire Alarm System Notification Appliances" article below.

Support up to 80 addressable panel annunciators. See "Addressable Panel Annunciators" below.

FACU Main Power Supply:

Provide addressable main power supply with universal input to accept either 120/240 VAC, 60 Hz, supplying all necessary power for FACU.

Include minimum four integral and programmable NACs.

Provide onboard patterns, zone coding, and synchronization (System Sensor, Wheelock, and Gentex).

Supply power distribution of each addressable main power supply that can be customizable to provide power for system, NAC, supporting circuits, auxiliary, and battery charging.

Up to three addressable main power supplies may be added within one FACU to expand power capacity.

Power supply supports up to 210 AH batteries.

Provide modular dress-panel and door design with interchangeable hinge locations.

Provide doors capable of reversible (left or right) hinge and lock.

Provide doors with interchangeable grey trim.

Basis of Design Products:

Notifier INSPIRE Series Model CPU-N16LD (N16x) expandable to 10 SLCs with 10-inch (254 mm) touchscreen display, and power supply with four NACs premounted on chassis compatible with CAB-5 enclosure.

Notifier Model PMB-AUX; up to two additional power supplies, one charging batteries, each supporting up to four NACs each.

Notifier CAB-5 Series enclosure with door for mounting; include required dress plates and finish trims.

Notifier Model SLM-318; signal loop module.

Emergency Voice/Alarm Communications System (EVACS) Panel:

Provide system listed and labeled as complying with UL 864.

Provide the following additional agency listings and approval requirements:

UL 464 (Audible Signaling Devices for Fire Alarm and Signaling Systems, Including Accessories).

UL 1481 (Power Supplies for Fire-Protective Signaling Systems).

UL 1638 (Visible Signaling Devices for Fire Alarm and Signaling Systems, Including Accessories).

UL 1711 (Amplifiers for Fire Protective Signaling Systems).

UL 1971 (Signaling Devices for the Deaf and Hard of Hearing).

UL 60950-1 (Information Technology Equipment - Part 1: General Requirements).

Provide digital voice command center located with FACU and containing equipment required for audio control, signaling and supervisory functions. This includes speaker zone indication and control, EVACS controller, and master microphone

Provide EVACS Controller which is field programmable without requiring return of components to manufacturer and without requiring use of external computers or other programming equipment.

Capable of supporting up to eight channels of simultaneous audio; each identified evacuation zone to allow broadcast of automatic audio or manual paging independent of other evacuation zones.

Provide factory recorded "library" of voice messages and tones in standard .WAV file format, which may be edited and saved on PCs running current Windows operating system.

Capable of control and supervision of 32 distributed digital amplifiers or 16 bulk digital distribution boards.

Provide communication channel which allows connection to digital amplifiers via manufacturer-approved copper wire media. Communications loop to be considered part of fire alarm system network and meet specified requirements for wiring methods and pathway survivability.

Include auxiliary input for external 1 Vrms audio source (e.g., music, and paging), configurable to mute during emergency events and power loss.

Provide switch points of command as follows, unless otherwise approved by Engineer and AHJ:

All-Call:  Provides manual paging for all zones simultaneously.

Total Evacuation:  Provides complete building-wide activation of audio and visual evacuation signals; restore on switch deactivation, signal silence, or system reset command.

Provide minimum of two switch points of manual controls per evacuation zone for manual paging and/or manual evacuation.

Manual Evacuation:  Activate audio and visual evacuation signals on selected zone. Restore on switch deactivation, signal silence, or system reset command.

Manual Paging:  Where active evacuation zone is selected, pause evacuation signal for manual page. Resume evacuation signal upon completion of paging function unless silence or reset command has been initiated.

In addition to required emergency messaging, provide switch points of command for minimum of three prerecorded messages for nonemergency all-call notifications including "event has cleared", "testing of system", and "clear from testing of system".

Door Release:  Provide switch points of command as required for unlocking of provisioned doors.

Provide minimum of six switch points of command for speaker bypass, visual bypass, elevator recall bypass, door control bypass, HVAC bypass, and auxiliary bypass.

Audio Transponders:

Audio hardware, including amplifiers, speaker circuit interfaces, power supplies, supervision hardware, cabinets, and battery backup systems may be configured to support multiple notification zones and packaged as audio transponders.

Transponders to be considered system control equipment and located, installed, and interfaced accordingly.

Components mounted in transponders to be listed and approved for installed configuration.

Provide maximum speaker circuit lengths with minimum signal loss for both current scope and future expansion consideration; maximum signal loss of minus 3 dB per speaker circuit, utilizing 70 Vrms audio for speaker circuits.

Distributed Digital Audio Amplifiers:

Interface with EVACS controller via individual address to allow for dedicated communication of audio, activation, and fault status.

Provide minimum quantity of two integrated speaker circuits per amplifier, each with unique system sub-address to allow for individual activation, control, and fault supervision. Systems that utilize addressable control or relay modules to provide speaker circuits are not permitted.

Provide capability to charge or supervise batteries and allow for inherent ground fault detection.

Provide capability for local mode alarm trigger for local activation and broadcast of evacuation tone on integrated speaker circuits in event of communication loss with system control hardware.

Include auxiliary input for external 1 Vrms audio source (e.g., music, and paging), configurable to mute during emergency events and power loss.

Provide capability to communicate detailed status of faults and conditions affecting operation of amplifiers and individual circuits. Systems that combine audio and communication into single points via addressable modules or other hardware are not permitted.

Provide dedicated backup amplifier board for each primary amplifier.

Bulk Digital Audio:

Provide digital audio distribution board to interface with EVACS controller via individual address to allow for dedicated communication of audio, activation, and fault status.

Provide four low-level audio outputs and eight high-level audio inputs for interface with audio amplifiers.

Provide minimum of four integrated speaker circuits, each with unique system sub-address to allow for individual activation, control, and fault supervision. Systems that utilize control or relay modules to provide speaker circuits are not permitted.

Capable of delivering full rated power to single integrated speaker circuit or distributed to multiple integrated speaker circuits.

Provide local UL 864 listed power supply with sufficient battery-charging capacity for bulk digital audio equipment contained within one enclosure.

Bulk Digital Audio Amplifiers:

Provide capability to communicate detailed status of faults and conditions. affecting operation of amplifiers and individual circuits. Systems that combine audio and communication into single points via addressable modules or other hardware are not permitted.

Capable of providing 100 W of 70 Vrms high-level audio for distribution through digital audio distribution board.

Provide dedicated backup amplifier board for each primary amplifier.

Basis of Design Products:

Notifier Model DVC-EM; digital multi-channel voice evacuation (EVACS) system integrated with FACU.

Notifier Model DVC-KDB; voice control keypad for DVC-EM with status indicators and 24 user-programmable buttons.

Fiber optic communication modules:

Notifier Model DS-FM; multi-mode fiber optic module for digital audio communications.

Distributed Digital Audio Amplifiers:

Notifier Model DAA2-5070; 50 W, 70 Vrms amplifier with four Class B or two Class A speaker circuits

Fiber Optic Communication Modules:

Notifier Model DS-FM; multi-mode fiber optic module for digital audio communications.

Backup Amplifier/Dual Channel Boards:

Notifier Model BDA-70V; 70 Vrms backup amplifier card.

Bulk Digital Audio:

Notifier Model DS-DB; bulk audio distribution board with eight Class B or four Class A speaker circuits.

Fiber Optic Communications Modules:

Notifier Model DS-FM; multi-mode fiber optic module for digital audio communications.

Notifier Model DS-AMP; bulk digital audio amplifier capable of 125 W at 25 Vrms or 100 W at 70 Vrms with transformer.

Notifier Model DS-BDA; backup amplifier card for DS-AMP 25 Vrms or 70 Vrms with transformer.

Notifier Model DS-XF70V; 70 Vrms transformer (required for each DS-AMP and DS-BDA).

Notifier Model AMPS-24; power supply.

High-Speed Networking:

LAN network architecture; peer-to-peer based firmware package, inherently regenerative communication format and protocol.

Support of up to 200 network nodes Class B or Class X operation with data communications rate of 12 Mbps (wire) or 100 Mbps (fiber).

Support high-speed network communications cards including ability to use combination wire/fiber communications using internal conversion cards without external converters.

Networks with Multimode Fiber Media:

Support 62.5/125 micrometer fiber (10 dB limit) or 50/125 micrometer fiber (6.5 dB limit).

Provide terminal box at each node for fiber demarcation.

Provide patch cables between terminal box and network interface module to facilitate troubleshooting and testing of connections.

Provide network capable of single channel digital voice and firefighters telephone, as well as panel-to-panel (same network media; wire and/or fiber) communications.

Basis of Design Products:

High-Speed Networks with Multimode Fiber Media:  Notifier Model HS-NCM-MF high-speed network communications module, fiber optic cable interface. Requires multi-mode 62.5/125 or 50/125 micrometer fiber.

High-Speed Networks with Mixed Medias:

Alarm Transmission and Integration:

Integrated Gateway:

California State Fire Marshal (CSFM) listed.

Fire Department New York City (FDNY) listed.

FCC compliant.

Provide gateway for connection to fire system panel or panel network, serving as interface between FACU, supervising/central station, cloud services and peripheral devices.

Able to read connected device system database for individual FACU or network of panels and automated report creation for supervising/central station.

Enable automatic supervising/central station setup without need for manual transfer of information to associate reporting codes with fire system points.

Reduce transfer times to supervising/central stations, dispatch centers, and emergency responders by eliminating need for additional transmission equipment (e.g., alarm-capture devices, and dialers) and associated processing delays while increasing reliability and accuracy of alarm transmission.

Enable detailed context sharing directly with first responders upon fire event to improve emergency response efficiency.

Capable of alarm transmission over AT&T or Verizon cellular networks. Selection of which cellular network will be user configured using communication modules selected based on strongest cellular signal available at location.

Capable of alarm transmission over Ethernet or Wi-Fi networks.

Enable integration directly to private radio communicator via Ethernet connection

Enable supplementary transmission of real-time data from fire alarm system to cloud service to enable remote monitoring of events via web application or mobile device application.

BACnet:  Support ability to send events from one Notifier panel or network of up to 15 panels using standard BACnet communications protocol.

Modbus:  Support ability to send events from single Notifier panel or network of up to 10 panels using standard Modbus communications protocol.

Support IP-based gateway to enable fire alarm panel or network of panels to be connected to PC-based graphical monitoring workstation via Internet or LAN.

CLSS Gateway:  Serves as gateway between workstation software and proprietary fire alarm network, uses that workstation as primary reporting station for proprietary fire alarm network, and translates proprietary fire alarm network’s panel and device data into data that can be interpreted proprietary workstation software application.

Proprietary Connection to Cloud-Based Testing and Inspection Platform:

Provide automated reports which comply with:

NFPA 10 (Standard for Portable Fire Extinguishers).

NFPA 25 (Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems).

NFPA 72 (National Fire Alarm and Signaling Code).

NFPA 2001 (Standard on Clean Agent Fire Extinguishing Systems).

Support ability to generate automated commissioning reports or test and inspection reports for installation or test and inspection personnel via cloud platform.

Reports should be stored in cloud, enabling appropriate stakeholders to retrieve test and inspection report immediately after completion of system commissioning or test and inspection.

Log and report method in which device disposition was captured;  either by event received from connected gateway, barcode scan, or manual user entry.

Automatically capture addressable devices connected to system ensuring that each addressable device is accounted for and tested. Include feature to automatically report devices as "passed" upon testing.

Allow importing of nonaddressable devices associated with system to ensure system devices are accounted for and tested.

Enable mobile service compatible with IOS and Android and have web-based access with Windows and MAC-based platforms without need to install software on dedicated network server.

Provide lockable plastic cabinet which is keyed identical to FACU.

Municipal/Remote Station/Relay Connections:

Municipal Tie Connection:  Provide quantity of interface zones, coding, timing, and other municipality-specific features as required by AHJ.

Alarm Transmission/Relay Interface Module:

Provide eight programmable relays on panel interface module.

Basis of Design Products:

​​Integrated Gateway;  Honeywell Model HON-CGW-MBB (CLSS gateway with enclosure) with Model 50160636-001 (keylock and cable kit) with support for monitoring via ​Rapid-Response-enabled​ supervising/central station.

Integrated Gateway Cellular Modules:  CCM-ATT-HON; AT&T cellular communication module or CCM-VZ-HON; Verizon cellular communication module.

Cloud-Based Testing and Inspection Platform:  Honeywell CLSS.

Alarm Transmission/Relay Interface Module; Honeywell Model TM-8; transmitter module.

PC-Based Graphical Life Safety Monitoring System:

System Description:

Connect UL 864 listed PC and software (monitoring and control) to Fire Alarm System, include interface devices to enable a fully functional system.

Additionally, provide connect cloud-connected Software (monitor only):

Connection via internet using Cellular, or IP connection, or intranet.

Ability to monitor Notifier ONYX and INSPIRE Series fire alarm panels using Honeywell CLSS gateway interface.

Ability to monitor third-party panels using Honeywell CLSS interface.

System includes, but not limited to, touch screen or LED wide screen monitor, connection to one PC-based graphical workstation(s), input/output devices, network communications media, auxiliary control devices, power supplies, and wire/fiber optic media as indicated on drawings.

Support variety of topologies and media, as well as provide industry-standard open architecture transport layer protocol.

Include redundant interface for proprietary fire alarm network for survivability.

Provide email functions capability to send graphical system information and real-time off-normal event notifications via email server to designated email accounts.

Provide supervised interface to Honeywell FACUs.

Electrically supervise system and monitor integrity of conductors.

Provide email functions capability to send graphical system information and real-time off-normal event notifications via email server to designated email accounts.

Provide supervised interface to Honeywell FACUs.

Electrically supervise system and monitor integrity of conductors.

Comply with requirements of NFPA 72 for Proprietary Signaling System Receiving Unit, except as modified and supplemented by this specification.

UL listed application software and hardware complete and ready for operation:

UL 294 (Access Control System Units).

UL 864 (Control Units for Fire Protective Signaling Systems).

UL 1076 (Proprietary Burglar Alarm Units and Systems).

UL 2017 (General-Purpose Signaling Devices and Systems).

Allow mixture of technologies and manufacturers’ equipment to operate on same network and provide operator with consistent look and operation for monitored equipment.

Using standard RS-232 ports on existing and future monitoring and control systems used by facility, system connects to and interprets status change data transmitted from ports and provides graphic annunciation, control, history logging and reporting.

Support Boolean logic for automatic event response.

Automated event response application provided to automatically perform actions across entire system based on network activity.

Event response application event responses or actions based on predefined user conditions using simplified Boolean logic.

Actions configured to be executed immediately or timed required.

Capability to page directly from workstation to any DVC installed on network.

Include interface to digital alarm communicator receivers for wide area network monitoring.

System Performance:

Network interface and reporting of individually monitored system’s status via user-friendly graphical user interface (GUI) based software workstation.

Software to operate under Microsoft Windows 10 Enterprise 64-bit operating system as manufactured by Microsoft Corporation.

GUI based software capable of graphically representing each facility being monitored with floor plans and icons depicting actual locations of various systems; and sensors’ locations as well as view system events in text mode.

Minimum resolution of 1920 X 1080 GUI display capable of showing enlarged floor plan views, key map representative of larger floor or site plan views, relationships of monitored facilities, current operator, number of fire, supervisory, prealarms, troubles, and security events within network as well as outstanding events and acknowledged events.

Software capacity of at least 1,000 screens/floor plans or as dictated by hard drive space and installed video and random access memory (RAM) for efficient operation.

Provide ability to float and dock windows to support dual monitors display.

Support graphic printing of data including graphical floor plans, system activity, history, and guidance text. Windows-compatible printer supported for graphics and report printer options.

Workstation software provides automatic navigation to screen containing icon that represents system or sensor in event of off-normal conditions.

System/sensor icon to indicate type of off-normal condition, flash, and change to color associated with off-normal condition (e.g., RED for ALARM, and YELLOW for TROUBLE).

Allow attachment of text (TXT) files, sound (WAV) files, image (BMP) files, and video (AVI) files to each system or sensor icon allowing additional information to be provided to system operator for responding to off-normal conditions. Software file attachment ability for each major event type, per device.

Allow importation of externally developed floor plans in Drawing Exchange Format (DXF), Windows Metafile (WMF), JPEG (JPG), Graphics Interchange Format (GIF) and Bitmap (BMP) format.

Provide automatic navigation to screen containing icon of system, sub-system, or individual sensor when events are initially annunciated. Operator navigation to screens containing outstanding events accomplished by selecting events from both acknowledged or unacknowledged events.

History Manager:  Record system events with time and date stamp as well as current system operator’s name.

Provide ability to store off-normal events experienced by various sub-systems that are monitored by system.

Events recorded with time and date stamp and system operator provided with ability to log predefined response or custom comment for each off-normal event and have that comment stored in history file with time, date, and operator name.

Provide ability to conduct searches and generate subsequent reports, based on all events for single system/device address, specific node, specific type of off-normal condition and date range (mm/dd/yy to mm/dd/yy) or combinations of these search parameters. Number of entries in history file that match determined search criteria will be displayed.

Automatically back-up history file at 2.5 million events.

Provide ability to preselect data fields for reporting and then save report as template, as well as schedule predefined report to print at designated time.

Provide operator ability to select number of days or number of months to back-up history.

Alarm Monitoring:  Provide for continuous monitoring of off-normal conditions regardless of current activity displayed on screen.

If operator is viewing history of sub-system and alarm condition occurs, system automatically navigates to graphic screen showing area where off-normal event is occurring.

Prioritize off-normal events defined by NFPA 72 into categories (e.g., fire alarms, troubles, supervisory alarms, prealarms, and security alarms).

Display running count of events by type in alarm summary window. Alarm summary window includes at least five counters, defaulted to alarm, prealarm, trouble, security, and supervisory events.

Show running list of unacknowledged events and acknowledged events and allow operator to acknowledge event by selecting on that event in unacknowledged events box. Unacknowledged and acknowledged events boxes contain abbreviated description of off-normal condition.

Details of condition may be viewed by selecting event in unacknowledged events box.

Allow attachment of user-definable text files, image files, video files, and sound files to each device/system monitored (for every event state) to facilitate operators and response personnel’s response to off-normal condition.

Record events to system’s hard drive. Minimum of 2.5 million events may be stored.

Provide ability to generate reports based on system history.

Allow system operator to enter custom comments up to 255 characters for each event and have those comments recorded in system history files.

Password protect software and provide for definition of security profiles for operator access control.

Software to contain provision for defining monitoring profiles of preselected nodes for monitoring. This includes provision for status types within selected nodes.

Includes configuration tool providing the following features:

Create and edit graphics.

Set up gateway connections and define their roles.

Set system operating mode.

Add and edit objects on screens.

Configure colors and sounds for status classes.

Gateway interfaces to have ability to be constructed in redundant configuration by having multiple Honeywell CLSS gateways on one network, monitored by multiple workstation clients.

Non-Cloud-Connected, Monitor and Control Aspects of System Software:

Ability to monitor and control Notifier ONYX and INSPIRE Series fire alarm panels using Honeywell CLSS gateway interface.

Ability to monitor and control Notifier ONYX and INSPIRE Series fire alarm panels using Honeywell CLSS gateway interface.

Sub-system not to rely on network for data processing required to perform their particular function. Each individual sub-system continues operation should disruption in communication with system be experienced.

Workstation:

Minimum Requirements:  IBM compatible Intel I7 processor on Microsoft Windows 10 OS platform. 16 GB of random access memory (RAM), solid-state hard drive with no less than 240 GB of storage space, minimum of 64 MB of video RAM, internal supervisory CPU watchdog board with audible annunciator, 100 Base-T Ethernet network interface card (NIC), 104-key keyboard, and mouse type pointing device with center wheel.

Support one or more Windows-compatible printers located and connected to each workstation for graphics and report printing.

Fire Alarm System Printers:  Support one Notifier Model PRN-7, 80-column dot matrix tractor feed industrial grade printer for event and date-stamped printouts of off-normal events and status changes per workstation.

Fire Alarm System Printers:  Support one Notifier Model PRN-7, 80-column dot matrix tractor feed industrial grade printer for event and date-stamped printouts of off-normal events and status changes per workstation.

Workstation industrial-grade computer listed for UL 864 (Control Units for Fire-Protective Signaling Systems). Workstation capable of annunciation of all fire detection points.

Support dual monitors and be supplied with 23-inch flat screen (610 mm) LED monitor(s) with integrated speakers.

Alarm annunciation to appear on all workstations and may be silenced at each local workstation.

System and associated equipment manufactured by single ISO 9001 U.S. manufacturer, or division thereof.

Computer capable of networking to additional computers and these computers capable of operating as workstations and/or gateways for local area or wide area networks.

Fire System Monitoring Network:

See "High-Speed Networking" in PART 2 above.

Integration Network:

Workstation Network:

Multiple workstation computers networked using Ethernet supporting use of TCP/IP protocol for local area systems.

Network capable of supporting multiple clients (e.g., workstations, configuration applications, and automated response applications), and Honeywell CLSS gateways.

Provide UL listed system components to communicate between clients and gateways over business computer network (shared IP).

Supply UL listed Ethernet hub for connection of multiple workstations, gateways, clients, and network printers.

Basis of Design Products:

Notifier ONYXWorks; UL-listed PC and software which connects to peer-to-peer fire alarm system network and provides control and monitoring.

Notifier ONYXWKS-HNMF; UL-listed PC, ONYXWorks View+Ctrl+Paging software, high-speed multi-mode fiber PC card; UL-listed monitor and mic not included.

Honeywell MON-23LCDW; 23-inch (610 mm) UL-listed Wide-Screen LED, WSXGA.

LAN-Connected Horizon; software on user provided PC which connects to CLSS gateway via Local Area Network and provides control and monitoring capabilities; Purchased as software license and downloaded via customer portal; one-time purchase with annual renewal.

Cloud-Connected Horizon; software on user provided PC which connects to cloud-hosted site for real-time system monitoring only. CLSS gateway (See "Alarm Transmission") is used to provide updates to cloud; purchased as software license and downloaded via customer portal; one-time purchase with annual renewal.

Addressable Panel Annunciators:

Comply with UL 864.

Provide plug-in terminal blocks for wiring connections.

Buttons and indicators capable of custom programming up to 60 points of annunciation.

Provide trichromatic LEDs (RGB) for custom colors as follows:  red, green, yellow, white, amber, blue, cyan, or purple.

Include 30 pushbuttons with two corresponding LEDs each.

Each pushbutton and LED can be programmed independently for different points or grouped with other indicators for cooperative operation.

Provide reindication of alarm or trouble by resounding and flashing when new conditions occur.

Provide local sounder for alarm and trouble conditions; include programming option to silence/acknowledge by pushbutton.

Capable of speaker control mode with integrated voice and FACU, allowing remote control for groups of multi-channels mapped to groups of multi-speakers.

Basis of Design Products:

Notifier Model ACM-30 fully customizable annunciator; independently configured buttons; up to 60 points; programmable LEDs.

Notifier Model CAB-4 or CAB-5 dress panel or compatible backbox for mounting.

Lamp Driver Modules:

Provide module with 60 LED outputs and 21 switch inputs per module for interface with graphic annunciators.

May be located up to 6,000 feet (1828 m) from FACU.

Inputs programmable for system acknowledge, signal silence, reset, initiate drill, activate or disable module, zone, audio control point, or bell circuit.

Switches configurable as momentary or toggle.

Support 5 VDC or 24 VDC LEDs.

Basis of Design Products:

Notifier Module LDM2-60 lamp driver module.

Remote LCD Display:

Comply with UL 864.

Capable of mimicking display of either FACU or network control display, based on connection or only information per specific zones.

Provide plug-in terminal blocks for wiring connections.

Provide 5-inch (127 mm) capacitive full color touchscreen LCD annunciator that displays all system events.

Block Acknowledge:  Support block acknowledge for trouble and disable conditions.

Provide programmer key switch for user authentication, providing ability to enable control inputs for acknowledge, silence, reset, and drill.

Provide configurable control buttons that are operational only when keyswitch is unlocked.

Provide six programmable buttons, each with descriptor/label, status indicator and configurable action (on/off, disable/enable).

Capable of being field programmed using PC configuration software.

Provide standard USB-C connection for software interface.

Basis of Design Products:

Notifier Model RLD network control annunciator, 5-inch (127 mm) color touch screen display; mounts in standard 3-gang backbox.

Network Control Display:

Comply with UL 864.

Capable of displaying information and controls similar to main FACU primary display (i.e., device type identifiers, individual point alarm, trouble or supervisory, zone, and custom alpha labels).

Provide plug-in terminal blocks for wiring connections.

Logical Operators:

Support logical functions, including at minimum:  AND (ALL), OR (ANY), NOT, ONLY1, COUNT (one-nine), and TIMERS.

Inputs for Operators:  Time of day, addressable devices, software points, and trouble codes.

Capable of differentiating operator inputs by specific device status (i.e., fire alarm, prealarm, nonalarm, disable, supervisory, and security).

Support up to 80 addressable panel annunciators. See "Addressable Panel Annunciators" above.

Support up to ten remote LCD displays. See "Remote LCD Display" above.

Fully field-programmable to display specific panels or all nodes on fire system network.

Capable of manually requesting point status information, disabling system inputs, and altering state of system outputs.

Provide high-definition 10-inch (254 mm) 1024 X 600 color touchscreen display.

Capable of displaying all events from all ​INSPIRE and ONYX​ nodes in fire system network.

Capacity to display intelligent system points and information for all events on fully utilized network of at least 300,000 points.

Provide history buffer capable of storing up to 10,000 events.

Provide color-coded notification icons based on event type.

Include audible and visible feedback with adjustable brightness solid-state LCD.

Include graphical QWERTY-style keypad on color, touchscreen display when alfa-numeric input is required.

Provide capability to scroll events by type using touchscreen  (i.e., fire alarm, supervisory alarm, and trouble).

Permit uploading of custom background image.

Provide event counters to indicate total number of events by type.

Provide standard USB connections for interfacing with PC-based software or USB devices, including USB-C, USB-Micro, and USB-A.

Passwords and Users:

Support five access levels (e.g., system operator, building maintenance user, technician user, admin user, master user) and up to 50 usernames and passwords.

Each role level access has default customizable permissions.

Only master password access password change screens.

Custom Buttons:  Support up to 32 programmable custom action buttons on LCD touchscreen display used to enable/disable or control outputs without use of additional hardware.

Basis of Design Products:

Notifier Model NCD network control display 1024 X 600 10-inch (254 mm) color touch screen display.

Notifier Model NBB-2 backbox (recessed- or surface-mounting capability).

Notification Appliance Circuit (NAC) Expansion:

Comply with UL 864.

Where NAC requirements exceed capacity of FACU, provide accessories as required for expansion.

Cabinet-mounted with capacity for providing 6 A 24 VDC notification appliance power and 5 Class B NAC outputs.

Include self-contained, lockable cabinet capable of storing 7 or 18 AH batteries.

Battery charger capacity capable of charging 7 AH to 33 AH sealed lead acid batteries.

Provide two activation inputs which allow for synchronization pass-through and can be associated with any combination of NAC outputs.

Fire alarm enclosure chassis-mounted with capacity for providing 12 A 24 VDC notification appliance power and 4 Class B NAC outputs.

Include chassis for mounting within fire alarm enclosure.

Provide two activation inputs which allow for synchronization pass-through.

Battery charger capacity capable of charging 7 AH to 26 AH sealed lead acid batteries.

Where Class A NACs are required, provide Class A module to enable each NAC to be configured as Class A.

Provide integral synchronization of both audio and visual circuits to match protocol assigned by FACU.

Basis of Design Products:

Honeywell Model HPF-PS6; 6 A notification power expander with five 24 VDC individually configurable outputs, red metal enclosure.

ZNAC-PS Class A output converter module.

Notifier Model HPFF12CM; 12 A chassis-mounted notification power expander with four 24 VDC NAC outputs, mounts within CAB-4 or EQ Series enclosure.

Notifier Model HPP31076; Class A adaptor for HPFF Series notification power expanders.

Fire Alarm System Printers:

Listed to UL 864 for use with fire alarm system.

Capable of providing written record of system events and status changes.

Power via 120 VAC emergency power.

Basis of Design Products:

Notifier Model PRN-7 fire alarm system printer, 24-pin dot-matrix.

Electromagnetic Door Holders:

Select according to door type and associated installation conditions.

Basis of Design Products:

Honeywell Model FM Series; model number selected according to application.

Fire Alarm System Initiating Devices

General Requirements:

Addressable Devices:  Individually identifiable by addressable FACU; suitable for connection to FACU SLCs. Provide address-setting means on device using rotary switches with simple numerical indicators. Devices which require proprietary tools or dip switches to address device will not be accepted.

Conventional (Nonaddressable) Devices:  Provide addressable monitor modules or two-wire detector zone modules (See "Addressable Interface Modules" article for Basis of Design Products) as indicated or as required for connection to addressable FACU. Unless devices are explicitly permitted to be connected together as one zone, provide separate addressable monitoring point for each device in order to be individually identifiable by addressable FACU.

Provide devices and associated accessories suitable for intended application and location to be installed. Unless otherwise indicated, use addressable devices and addressable monitor modules only in clean, dry, indoor, nonhazardous locations.

Surface-Mounted Devices:  Provide manufacturer's accessory surface mount backboxes or suitable outlet/device box.

Devices for Outdoor and Damp/Wet Locations:  Weatherproof, suitable for outdoor use; provide manufacturer's accessory backboxes and enclosures in accordance with product listing.

Devices for Hazardous (Classified) Locations:  Listed and labeled as suitable for classification of installed location.

Self-Testing Devices:

Capable of CLSS identifying issues associated with integrity or ability for smoke detector to properly detect smoke (e.g., dust cap not removed or tampering with detector by obstructing smoke chamber.

Capable of providing functional and smoke entry tests using self-test function.

Detector transmits 'wireless beacon activated' only during self-test mode.

Designed to communicate with CLSS app to prove successful completion of visual inspection.

Manual Fire Alarm Boxes (Pull Stations):

Description:  Noncoded manual signaling boxes listed and labeled as complying with UL 38.

Alarm Initiation:  Configured for general alarm initiation unless otherwise indicated; presignal stations (where indicated) require use of key to initiate general alarm.

Operation:  Dual-action unless otherwise indicated; first requires pushing in then pulling down of lever.

Color:  Red, in accordance with NFPA 72.

Station Reset:  Requires use of key or tool.

Basis of Design Products:

Manual Pull Stations:

Notifier Model NBG-12LX addressable manual pull station, indoor rated, dual-action, key lock.

Surface Mount Backboxes:

Spot-Type Detectors:

Addressable Detectors:

Comply with "General Requirements for Addressable Devices."

Provide LED indication of normal operation/regular communication with FACU condition.

Furnished with output for remote LED alarm indicator.

Utilizes plug-in mounting to separate base with tamper-resistant feature; compatible with available sounder, relay, and isolator bases; provide base as indicated or as required.

Smoke Detectors:

Listed and labeled as complying with UL 268.

Use photoelectric (light-scattering) principal to measure smoke density.

Provide data to FACU representing analog level of smoke density.

Self-Testing Smoke Detectors:

Self-generate controlled amount of smoke into chamber, testing optic response to real smoke simulation.

Detector measures dilution of smoke within set time limits to determine if there is masking preventing smoke from entering chamber.

Generate detector alarm condition upon smoke entering chamber.

Detector generates trouble condition if testing chamber is blocked.

Thermal (Heat) Detectors:

Listed and labeled as complying with UL 521.

Provide fixed thermal sensor which activates at 135 degrees F (57 degrees C).

Self-Testing Thermal (Heat) Detectors:

Self-generate energy into internal thermistor, allowing register heat identification.

Detector measure cooling of heating element after cycle complete.

Generate detector alarm condition upon introduction of heat from thermistor.

Detector generates trouble condition if thermistor does not detect heat.

Carbon Monoxide Detectors:

Listed and labeled as complying with UL 2075.

Comply with requirements for addressable detectors unless otherwise noted for areas where addressable devices are not feasible.

Furnished with end-of-life notification.

Combination and Multi-Criteria Detectors:

Comply with respective requirements for each detection method.

Self-Testing Multi-Criteria Detectors:  Comply with respective self-testing requirements.

Detector/Base Color:  White, unless otherwise indicated.

Basis of Design Products:

Smoke Detectors:

Notifier Model FSP-951 addressable smoke detector, indoor rated, photoelectric, integral drift compensation, self-diagnostics, transient rejection, local test via application of external magnet.

Notifier Model FSP-951T addressable smoke/thermal detector, indoor rated, photoelectric, integral drift compensation, self-diagnostics, transient rejection, local test via application of external magnet.

Notifier Model FSP-951-SELFT self-test addressable smoke detector, indoor rated, photoelectric.

Thermal (Heat) Detectors:

Notifier Model FST-951 addressable thermal detector, indoor rated, fixed temperature, 135 degrees F (57 degrees C), RTI rating for installation of FAST or better, local test via application of external magnet.

Notifier Model FST-951H addressable thermal detector, indoor rated, fixed temperature, 190 degrees F (88 degrees C), RTI rating of QUICK or better, local test via application of external magnet.

Notifier Model FST-951R addressable thermal detector, indoor rated, fixed temperature 135 degrees F (57 degrees C) and rate-of-rise, 15 degrees F (8.3 degrees C) per minute, local test via application of external magnet.

Notifier Model FST-951-SELFT self-test addressable thermal detector, indoor rated.

Carbon Monoxide Detectors:

Notifier Model FSCO-951 addressable carbon monoxide detector, indoor rated.

Combination/Multi-Criteria Detectors:

Notifier Model FPC-951 addressable smoke/carbon monoxide detector, indoor rated; photoelectric smoke sensor; automatic drift-compensation.

Notifier Model FPTI-951 addressable smoke/thermal detector, indoor rated; photoelectric smoke sensor; fixed temperature thermal sensor, 135 degrees F (57 degrees C), automatic sensitivity adjustment.

Notifier Model FCO-951 addressable multi-criteria smoke/thermal/carbon monoxide detector, indoor rated; photoelectric smoke sensor; fixed temperature thermal sensor, 135 degrees F (57 degrees C); automatic drift-compensation.

Notifier Model FSP-951T-SELFT self-test addressable smoke/thermal detector, indoor rated.

Bases for Addressable Detectors:

Notifier Model B300-6 Series standard base, flanged low-profile.

Notifier Model B200S-LF-WH Series low-frequency sounder base, white.

Notifier Model B200S-WH Series sounder base, white.

Notifier Model B224RB-WH Series relay base, one Form C contact for auxiliary functions, white.

Notifier Model B224BI-WH Series plug-in isolator base, white.

Notifier Model B501-WHITE Series standard base, unflanged.

Detector Accessories:

Notifier Model RA100Z remote indicator; provides LED indication of alarm condition.

Up to two remote indicators may be connected to single detector.

Duct Smoke Detectors:

Listed and labeled as complying with UL 268A.

Sampling Tubes:  Select as required for installation in duct to be monitored.

Remote Test Stations:  Provide remote test station for each duct smoke detector unless explicitly indicated as not required. Unless otherwise indicated, use remote test stations only in clean, dry, indoor, nonhazardous locations.

Basis of Design Products:

Addressable duct smoke detector assembly for indoor applications consisting of the following:

Notifier Model DNR duct smoke detector housing, indoor rated.

Notifier Model FSP-951R addressable smoke detector, indoor rated, photoelectric, remote test capable.

Notifier DST Series sampling tube of appropriate length.

Addressable duct smoke detector assembly for outdoor applications consisting of the following:

Notifier Model DNRW duct smoke detector housing, weatherproof.

Notifier Model FSP-951R addressable smoke detector, indoor rated, photoelectric, remote test capable.

Notifier DST Series sampling tube of appropriate length.

Notifier Model DH400OE-1 weatherproof enclosure for housing components listed above. Fill interior of enclosure with appropriate insulation media to minimize condensation.

Notifier Model RTS151 remote test station for addressable detectors; allows for detector test (via external magnet application) and reset; provides LED indication of alarm condition.

Notifier Model RTS151KEY remote test station for addressable detectors; allows for detector test (via external magnet application) and key reset; provides LED indication of alarm condition.

Beam Smoke Detectors:

Listed and labeled as complying with UL 268.

Provide coverage for 16 to 328 feet (5 to 100 m) standard.

Use advanced smoke imaging techniques to avoid false alarms from partial and sudden blockage from foreign object intrusion.

Transmitter unit including heating kit (nonenabled by default) for prevention of condensation. Provide 24 VDC power source for heater and enable heater where indicated.

Provide automatic drift compensation and sensitivity threshold level settings.

Provide four automatic sensitivity levels (25, 30, 40, and 50 percent).

UL listed operating temperature from 32 degrees F (100 degrees F).

Provide paintable cover.

Basis of Design Products:

Notifier Model FS-OSI-RI addressable beam video-imaging detector, single-ended reflected beam type with transmitter unit and reflector; protection range of 16 to 328 feet (5 to 100 m) with standard reflector; beam adjustment angle of plus/minus 10 degrees. Furnish accessories as indicated or as required.

Notifier Model 6500-MMK multi-mount kit, provides ceiling or wall mounting capability with increased angular adjustment.

Notifier Model BEAMHKR heating kit for reflector for prevention of condensation; requires separate 24 VDC power source for heater.

Notifier Model RTS151 remote test station for addressable detectors; allows for detector test (via external magnet application) and reset; provides LED indication of alarm condition.

Notifier Model RTS151KEY remote test station for addressable detectors; allows for detector test (via external magnet application) and key reset; provides LED indication of alarm condition.

Air-Sampling Smoke Detection Systems:

Design and provide smoke detection system suitable for application and coverage area indicated, consisting of smoke detector unit with aspirator/fan that continuously draws air into sensing chamber through connected sampling pipe network and associated sampling ports.

Comply with NFPA 72 and list and label as complying with UL 268.

Comply with applicable requirements of NFPA 76 for very early warning fire detection (VEWFD).

Detector Unit:

Sensitivity:  Programmable; capable of meeting NFPA 76 requirements for Very Early Warning Fire Detection (VEWFD) even if system is designed and programmed for to be less stringent.

Smoke Detection Method:  Laser-based light scattering mass detection.

Alarm Levels:  Programmable; as indicated or as required to perform alert, prealarm action, and alarm functions; minimum of four.

Display:  Provides local annunciation of detector trouble and alarm status.

Sampling Pipe Network:

Use manufacturer's recommended sampling pipe and fittings; plenum rated; identified in accordance with NFPA 72.

Designed using manufacturer's product-specific design software or based on manufacturer's pre-engineered design suitable for intended application.

FACU Interface:

Communicates up to five levels of events to FACU via SLC interface for display and use in control-by-event system programming.

Allows access to real-time status information at FACU including alarms and faults.

Displays real-time read status of percent of alarm.

Capable of initiating detector service mode from FACU.

Capable of resetting detector airflow baselines from FACU.

Basis of Design:  Xtralis VESDA-E Aspirating Smoke Detection.

Xtralis VESDA-E VEP Series; Model VEP-A00-1P-NTF-VN:  Addressable, single pipe, coverage up to 10,760 sq feet (1,000 sq m).

Xtralis VESDA-E VEP Series; Model VEP-A00-P-NTF-VN:  Addressable, four pipes, coverage up to 21,520 sq feet (2,000 sq m).

Xtralis VESDA-E VEU Series; Model VEU-A10-NTF-VN:  Addressable, four pipes, 3.5-inch (89 mm) LCD display, coverage up to 69,965 sq feet (6,500 sq m).

Xtralis VESDA-E VEU Series; Model VEU-A11-NTF-VN:  Addressable, four pipes, coverage up to 69,965 sq feet (6,500 sq m).

Xtralis VESDA-E VEA Series; Model VEA-040-A10-NTF-UL:  Addressable, four pipes, 3.5-inch (89 mm) LCD display, coverage up to 36,000 sq feet (3,345 sq m).

Xtralis VESDA-E VES Series; Model VES-A00-P-NTF-VN:  Addressable, four pipes, increased alarm thresholds and relay outputs, autoLearn (smoke/flow), coverage up to 21,520 sq feet (2,000 sq m).

Xtralis VESDA-E VES Series; Model VES-A10-P-NTF-VN:  Addressable, four pipes, 3.5-inch (89 mm) LCD display, increased alarm thresholds and relay outputs, autoLearn (smoke/flow), coverage up to 21,520 sq feet (2,000 sq m).

Fire Alarm System Interface Modules

Fire alarm system accessory equipment listed and labeled as complying with UL 864.

Provide addressable interface modules as indicated or required for fire alarm and nonfire alarm interfaced systems.

Individually identifiable by addressable FACU; suitable for connection to FACU SLCs. Provide address-setting means on device using rotary switches with simple numerical indicators. Devices which require proprietary tools or dip switches to address device will not be accepted.

Provide addressable modules suitable for connection to FACU SLCs.

Unless otherwise indicated, use addressable modules only in clean, dry, indoor, nonhazardous locations.

Addressable Monitor Modules:  Unless devices are explicitly permitted to be connected together as one zone, provide separate addressable monitor module for each conventional dry-contact input device in order to be individually identifiable by addressable FACU.

Addressable Control Modules:  Provide as indicated or as required for selective control of notification appliances.

Addressable Releasing Control Modules:  Provide as indicated or as required for control of listed solenoids in releasing applications.

Addressable Firefighter Telephone Module:  Provide as indicated or as required for selective control of Firefighter Telephone locations.

Addressable Relay Modules:  Provide as indicated or as required to perform necessary functions via dry-contact interface. Where load exceeds module contact rating, provide accessory power isolation relays suitable for load as required.

Addressable Signaling Line Circuit (SLC) Isolating Modules:  Provide as indicated or as required to automatically isolate short circuits on connected sections of SLC loops and allow other sections to continue to function normally. Provide automatic reset upon correction of short circuit.

Basis of Design Products:

Addressable Monitor Modules:

Notifier Model FMM-1 addressable monitor module; single monitoring point, supervises one Class A or Class B circuit of conventional dry-contact input devices; uses single module address on SLC; mounts to nominal 4-inch (102 mm) square or 2-gang box, includes white finish cover.

Notifier Model FDM-1 addressable monitor module; two monitoring points, supervises two Class B circuits of dry-contact input devices; uses two module addresses on SLC; mounts to nominal 4-inch (102 mm) square or 2-gang box, includes white finish cover.

Notifier Model FMM-101 addressable monitor module, miniature; single monitoring point, supervises one Class B circuit of conventional dry-contact input devices; suitable for installation within appropriately sized device box behind monitored unit; uses single module address on SLC.

Notifier Model XP10-M addressable multi-monitor module; ten monitoring points, supervises ten Class B circuits of dry-contact input devices; uses ten module addresses on SLC; mounts to CHS-6 chassis within enclosure.

Addressable Control Modules:

Notifier Model FCM-1 addressable control module; single supervised control output, Class A or Class B, suitable for controlling 24 VDC NAC and speakers up to 70.7 Vrms; requires separate power; uses single module address on SLC; mounts to nominal 4-inch (102 mm) square or 2-gang box, includes white finish cover.

Notifier Model XP6-C addressable multi-control module; six Class B or three Class A supervised control outputs, suitable for controlling 24 VDC NAC and speakers up to 70.7 Vrms; requires separate power; uses six module addresses on SLC; mounts to CHS-6 chassis within enclosure.

Addressable Releasing Control Module:

Notifier Model FCM-1-REL addressable releasing control module; single supervised solenoid release output, Class A or Class B, suitable for connection to one 24 VDC solenoid or up to two 12 VDC solenoids (in series) listed for releasing service; utilizes redundant protocol; requires separate 24 VDC power; uses single module address on SLC; mounts to nominal 4-inch (102 mm) square or 2-gang box, includes white finish cover.

Addressable Firefighter Telephone Module:

Notifier Model FTM-1 addressable firefighter telephone control module; monitors two firefighter telephones, Class A or Class B; uses single module address on SLC; mounts to nominal 4-inch (102 mm) square or 2-gang box.

Addressable Relay Modules:

Notifier Model FRM-1 addressable relay module; two Form C dry contacts that switch together; uses single module address on SLC; mounts to nominal 4-inch (102 mm) square or 2-gang box, includes white finish cover.

Notifier Model XP6-R addressable multi-relay module; Six individually programmable Form C dry contacts; uses six module addresses on SLC; mounts to CHS-6 chassis within enclosure.

Addressable Multi-Input/Output Modules:

Notifier Model FDRM-1 addressable multi-input/output module; two monitoring points, supervises two Class B circuits of dry-contact input devices; two Form C dry contacts that operate independently; uses up to four module addresses on SLC; mounts to nominal 4-inch (102 mm) square or 2-gang box, includes white finish cover.

Addressable Signaling Line Circuit (SLC) Isolating Modules:

Notifier Model ISO-X addressable signaling loop circuit (SLC) isolating module; does not use any module addresses on SLC; mounts to nominal 4-inch (102 mm) square or 2-gang box, includes white finish cover.

Notifier Model ISO-6 addressable signaling loop circuit (SLC) isolating module; does not use any module addresses on SLC; mounts on CHS-6 chassis within enclosure.

Accessories:

Notifier Model PR-1 power isolation relay for loads exceeding relay module contact ratings; operating voltage of 18-35 VDC, 18-35 VAC, or 120 VAC; LED visible indication of relay coil energization.

Fire Alarm System Notification Appliances

Notification Appliances - General Requirements:

Provide signaling devices listed for fire-protective service and intended operating mode (public or private); suitable for connection to FACU notification NAC.

Provide addressable control modules as indicated or as required for selective control of notification appliances.

Provide notification appliances and associated accessories suitable for intended application and location to be installed. Use notification appliances only according to listed mounting (i.e., ceiling or wall mounted).

Surface-Mounted Notification Appliances:  Provide manufacturer's accessory surface mount backboxes or suitable outlet/device box.

Notification Appliances for Outdoor and Damp/Wet Locations:  Weatherproof, suitable for outdoor use; provide manufacturer's accessory backboxes and enclosures in accordance with product listing.

Notification Appliance Derating:  Account for device derating adjustments in accordance with listing where applicable, including but not limited to the following.

Where accessory protective guards, and enclosures are utilized.

Where required by field conditions (e.g., ambient temperature).

Notification Appliances Colors:

See mounting configuration indicated by floor plan drawing symbols.

Wall-Mounted:  ​White​.

Ceiling-Mounted:  White.

Visible Notification Appliances:

Public Mode Operation:  Listed and labeled as complying with UL 1971.

Strobes:  Clear or nominal white lens with flash rate of 1 Hz unless otherwise indicated or required; xenon light source with maximum pulse duration of 0.2 seconds; candela rating as indicated.

Audible Notification Appliances:

Listed and labeled as complying with UL 464.

Rated Sound Pressure Level:  As required to achieve design sound pressure levels, but not less than 75 dB(A) at 10 feet (3.1 m) for public mode operation or 45 dB(A) at 10 feet (3.1 m) for private mode operation in accordance with UL 464.

Horns:  Selectable tone, including at minimum NFPA 72-compliant temporal 3 pattern and continuous; minimum of two selectable volume levels.

Low-Frequency Sounders:  Listed for producing low frequency (520 Hz) alarm signal for sleeping areas in accordance with NFPA 72; selectable tone, including at minimum NFPA 72-compliant temporal 3 pattern and continuous.

Speakers for Emergency Voice/Alarm Communications Systems (EVACS):

Listed and labeled as complying with UL 1480.

Rated Sound Pressure Level:  As required to achieve design sound pressure levels, but not less than 75 dB(A) at 10 feet (3.1 m) in accordance with UL 1480.

Frequency Range:  400 to 4,000 Hz minimum in accordance with UL 1480; listed for producing 520 Hz low frequency alarm signal for sleeping areas in accordance with NFPA 72.

Speaker Voltage:  Field-selectable (25 Vrms, 70.7 Vrms); matched to audio distribution circuit.

Furnished with minimum of four field-selectable power taps.

Combination Notification Appliances:  Comply with respective requirements for each signaling method.

Exterior Notification:

Fire Alarm Visible Notification:  Provide strobe beacon with red lens; interface to dedicated NAC or addressable control module, 24 VDC, supervised.

Sprinkler System Waterflow Visible Notification:  Provide strobe beacon with clear lens; interface to dedicated NAC or addressable control module, 24 VDC, supervised; same circuit as sprinkler system waterflow audible notification where provided.

Sprinkler System Waterflow Audible Notification:  Provide bell; interface to dedicated NAC or addressable control module, 24 VDC, supervised; same circuit as sprinkler system waterflow visible notification where provided.

Basis of Design Products:

Strobes:

Notifier Model SWLED strobe, indoor rated, wall-mounted, white, selectable candela output (15, 30, 75, 95, 110, 135, 185 at 24 VDC nominal).

Notifier Model SGWLED strobe, compact, indoor rated, wall-mounted, white, selectable candela output (15, 30, 75, 95, 110, 135, 185 at 24 VDC nominal).

Notifier Model SWK strobe, weatherproof (includes backbox), wall-mounted, white, selectable candela output (15, 15/75, 30, 75, 95, 110, 115 at 24 VDC nominal).

Notifier Model SCWLED strobe, indoor rated, ceiling-mounted, white, selectable candela output (15, 30, 75, 95, 115, 150, 177 at 24 VDC nominal).

Notifier Model SCWKLED strobe, weatherproof (includes backbox), ceiling-mounted, white, selectable candela output (15, 15/75, 30, 75, 95, 110, 115 at 24 VDC nominal).

Notifier Model SCWHKLED-P strobe, plain, weatherproof (includes backbox), wall-mounted, white, selectable candela output (135, 150, 177, 185 at 24 VDC nominal).

Notifier Model SWLED-CLR-ALERT strobe, "ALERT" marking, clear lens, indoor rated, wall-mounted, white, selectable candela output (15, 30, 75, 95, 110, 135, 185 at 24 VDC nominal).

Horns:

Notifier Model HWL horn, indoor rated, wall-mounted, white.

Notifier Model HGRL horn, compact, indoor rated, wall-mounted, white.

Notifier Model MHW mini-horn, indoor rated, white.

Notifier Model HWK horn, weatherproof (includes backbox), wall-mounted, white.

Notifier Model MHW mini-horn, indoor rated, white.

Horn/Strobes:

Notifier Model P2WLED horn/strobe, indoor rated, wall-mounted, white, selectable candela output (15, 30, 75, 95, 110, 135, 185 at 24 VDC nominal).

Notifier Model P2GWLED horn/strobe, compact, indoor rated, wall-mounted, white, selectable candela output (15, 30, 75, 95, 110, 115, 135, 150, 177, 185 at 24 VDC nominal).

Notifier Model P2GWKLED horn/strobe, weatherproof (includes backbox), wall-mounted, white, selectable candela output (15, 15/75, 30, 75, 95, 110, 115 at 24 VDC nominal).

Notifier Model P2WHK horn/strobe, weatherproof (includes backbox), wall-mounted, white, selectable candela output (135, 150, 177, 185 at 24 VDC nominal).

Notifier Model PC2WLED horn/strobe, indoor rated, ceiling-mounted, white, selectable candela output (15, 30, 75, 95, 115, 150, 177 at 24 VDC nominal).

Notifier Model PC2WKLED horn/strobe, weatherproof (includes backbox), ceiling-mounted, white, selectable candela output (15, 15/75, 30, 75, 95, 110, 115 at 24 VDC nominal).

Notifier Model PC2WHK horn/strobe, weatherproof (includes backbox), ceiling-mounted, white, selectable candela output (135, 150, 177, 185 at 24 VDC nominal).

Low-Frequency Sounders:

Notifier Model HWL-LF low-frequency sounder, indoor rated, wall-mounted, white.

Notifier Model HGWL-LF low-frequency sounder, compact, indoor rated, wall-mounted, white.

Notifier Model HCWL-LF low-frequency sounder, compact, indoor rated, ceiling-mounted, white.

Low-Frequency Sounder/Strobes:

Notifier Model P2WL-LF low-frequency sounder/strobe, indoor rated, wall-mounted, white, selectable candela output (15, 30, 75, 95, 110, 135, and 185 at 24 VDC nominal).

Notifier Model PC2WL-LF low-frequency sounder/strobe, indoor rated, ceiling-mounted, white, selectable candela output (15, 30, 75, 95, 115, 150, and 177 at 24 VDC nominal).

Speakers:

Notifier Model SPWL speaker, indoor rated, wall-mounted, white.

Notifier Model SPWK speaker, weatherproof (includes backbox), wall-mounted, white.

Notifier Model SPCW8 speaker, dual-voltage, indoor rated, ceiling-mounted, white.

Notifier Model SPCWK speaker, weatherproof (includes backbox), ceiling-mounted, white.

Speaker/Strobes:

Notifier Model SPSWL speaker/strobe, indoor rated, wall-mounted, white, selectable candela output (15, 30, 75, 95, 110, 135, 185 at 24 VDC nominal).

Notifier Model SPSWK speaker/strobe, weatherproof (includes backbox), wall-mounted, white, selectable candela output (15, 15/75, 30, 75, 95, 110, 115 at 24 VDC nominal).

Notifier Model SPSCWL speaker/strobe, indoor rated, ceiling-mounted, white, selectable candela output (15, 30, 75, 95, 115, 150, 177 at 24 VDC nominal).

Notifier Model SPSCWK speaker/strobe, weatherproof (includes backbox), ceiling-mounted, white, selectable candela output (15, 15/75, 30, 50, 75, 95, 110, 115 at 24 VDC nominal).

Notifier Model SPSWLED-CLR-ALERT speaker/strobe, "ALERT" marking, clear lens, indoor rated, wall-mounted, white, selectable candela output (15, 30, 75, 95, 110, 135, 185 at 24 VDC nominal).

Bells:

Notifier Model SSM24-6 bell, 6-inch (15.24 cm) nominal, red, 24 VDC.

Surface Mount Backboxes:

Notifier Model SBBWL surface mount backbox for indoor rated, wall-mounted horn, strobe, or horn/strobe, white.

Notifier Model SBBCWL surface mount backbox for indoor rated, ceiling-mounted horn, speaker, strobe, horn/strobe, or speaker/strobe, white.

Fire Alarm System Accessories

Cables for Network Connections:

Comply with manufacturer's minimum requirements.

Surge Protection:

Line Voltage Surge Protection:  UL 1449 listed; provide for each line voltage circuit that supplies operating power for fire alarm system control equipment (e.g., FACU, field booster panels, nodes, and transponders).

PART 3  EXECUTION

Installation

Install products in accordance with NFPA 72, NFPA 70, state and local codes, manufacturer's instructions, and as indicate on drawings.

Install products in accordance with applicable requirements of NECA 1 (general workmanship).

Provide grounding and bonding in accordance with manufacturer's recommendations; see Section 260526.

Install firestopping to preserve fire resistance rating of partitions and other elements; see Section 078400.

Identify system wiring, components, and overcurrent protective devices for branch circuits serving fire alarm system; see Section 260553.

Conceal conduit, junction boxes, and conduit supports and hangers in finished areas. Conceal or expose conduit, junction boxes, and conduit supports and hangers in unfinished areas; maintain code required access.

Do not install smoke detectors before system programming and test period. If construction is ongoing during this period, take measures to protect smoke detectors from contamination and physical damage.

Mount fire detection and alarm system devices, control panels, and remote annunciators flush or surface as indicated.

Ensure installation locations of devices and notification appliances are in accordance with local codes, standards, and ensure manual stations are suitable for surface mounting or semi-flush mounting as indicated on drawings. Install not less than 42-inches (1.07 m), nor more than 48-inches (1.22 m), above finished floor measured to operating handle.

Field Quality Control

See Section 014000 - Quality Requirements for additional requirements.

Notify Owner and Engineer at least two weeks prior to scheduled inspections and tests.

Notify AHJ and comply with their requirements for scheduling inspections and tests and for observation by their personnel.

Provide equipment, tools, supplies, two-way radios, and personnel required to accomplish inspection and testing.

Prepare and start system in accordance with manufacturer's instructions.

Program system parameters according to project requirements.

Perform initial and acceptance inspection and testing in accordance with NFPA 72 and requirements of AHJ; document each inspection and test.

Test for proper interface with other systems.

Correct defective work, adjust for proper operation, and retest until entire system complies with contract documents.

Cleaning

Clean exposed surfaces to remove dirt, paint, or other foreign material and restore to match original factory finish.

Closeout Activities

See Section 017800 - Closeout Submittals for closeout submittals.

See Section 017900 - Demonstration and Training for additional requirements.

Demonstration:  Demonstrate proper operation of system to Owner and correct deficiencies or make adjustments as directed.

Be prepared to conduct required tests.

Have at least one copy of operation and maintenance data, copy of project record drawings, input/output matrix, and operator instructions available during demonstration.

Have manufacturer's authorized representative present during demonstration.

Demonstration may be combined with inspection and testing required by AHJ.

Training:  Owner Personnel Instruction:

Provide the following instruction to designated Owner personnel:

Hands-On Instruction:  On-site, using operational system.

Classroom Instruction:  Owner furnished classroom, on-site or at other local facility.

Basic Operation:  One 1-hour session pre-closeout for attendant personnel, security officers, and engineering staff; combination of classroom and hands-on.

Furnish services of instructors and teaching aids; have copies of operation and maintenance data available during instruction.

Protection

Protect installed system components from subsequent construction operations.

Maintenance

See Section 017000 - Execution and Closeout Requirements for additional requirements relating to maintenance service.

Provide to Owner as alternate to base bid, a separate maintenance contract for service and maintenance of fire alarm system for entire manufacturer's warranty period to include work described below; include complete description of preventive maintenance, systematic examination, adjustment, inspection, and testing, with detailed schedule.

Perform routine inspection, testing, and preventive maintenance required by NFPA 72, including:

Maintenance of fire safety interface and supervisory devices connected to fire alarm system.

Repairs required outside of warranty as approved by Owner.

Record keeping required by NFPA 72 and AHJ.

Provide trouble call-back service upon notification by Owner:

Provide on-site response within four hours of notification.

Include fee schedule for call-back service during and outside normal working hours; include definition of normal working hours.

Maintain on-site log listing date and time of each inspection and call-back visit, condition of system, nature of trouble, correction performed, and parts replaced.

- END OF SECTION